| INFORMATION | PLAN CHECK NO.: |  |  | EXPIRATION DATE: |  |  |  |  |  |  |  | STATUS: |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PROJECT ADDRESS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | WORK DESCRIPTION: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | APPLICANT’S NAME: |  |  |  |  |  |  | TEL. NO.: |  |  |  |  |  |  |
|  | ADDRESS: |  |  |  |  |  |  | EMAIL: |  |  |  |  |  |  |
|  | USE | OCCUPANCY GROUP | FLOOR AREA |  | OCCUPANT LOAD | TYPE OF CONSTR. |  |  |  | NO. OF STORIES |  |  |  | FIRE SPRINKLER LOCATION |
| INSTRUCTIONS | Your application for a permit, together with plans and specifications, has been examined and you are advised that the issuance of a permit is withheld for the reasons hereinafter set forth. The approval of plans and specifications does not permit the violation of any sections of the Building Code or other local ordinances or state laws. In an effort to streamline the plan review process, please follow the steps outlined below to ensure that there is no delay in processing your application and reviewing your responses to these plan check comments. - Comments with circled item numbers apply to this plan check. - Revised plans and calculations shall incorporate or address all comments marked on the original checked set of plans, calculations, and this plan review checklist. Provide a written response to each comment and show where and how it has been addressed. Identify the sheet number and detail or reference note on the revised plans where the corrections are made. Time spent searching for the corrected items on the revised plans or calculations will delay the review and approval process. Once all comments on the plans, calculations, and this checklist have been addressed, contact the plan check staff to schedule an appointment to review the changes made. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | PLAN REVIEWER: |  |  |  |  |  | TEL. NO.: |  |  |  |  |  |  |  |
|  | ADDRESS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | EMAIL: |  |  |  |  |  | WEBSITE: |  |  |  |  |  |  |  |
|  | Should you have any questions or need clarification pertaining to the comments made on your project, you may contact the plan check staff by telephone from to M T W TH F. - Bring the original checked set of plans and calculations along with this checklist to the meeting. Do not schedule an appointment meeting with the plan check staff until all comments have been addressed. - Incomplete, indefinite or faded drawings or calculations will not be accepted. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NOTE | Numbers within the parenthesis ( ) refer to the section of the applicable code. 2013 California Building Code (CBC), Table (T), 2013 California Plumbing Code (CPC), 2013 California Mechanical Code (CMC), 2013 California Fire Code (CFC) |  |  |  |  |  |  |  |  |  |  |  |  |  |

- CHAPTER 1 GENERAL PROVISIONS

- A.	PERMIT APPLICATION

- Provide a fully dimensioned plot plan to scale, in ink and copy it to the plot plan sheet provided by the department. Include the following information as applicable: project address, type of construction, number of stories, use and occupancy of the building, fire separation distance or setback of building to property lines or other buildings on the lot, lot size and dimensions, street center line, alley, # of parking spaces, location of all other buildings on the lot, legal description, and permit application number.

- Valuation provided or determined during the initial submittal process was not accurate. Valuation is revised to $____________________. Pay additional required plan check fee of $____________________.

- Provide complete and correct legal description (i.e., Tract, Lot, Block, APN, metes and bounds, etc.).

- Provide complete information for (applicant) (owner) (engineer) (architect) (contractor) (______________).

- Separate permit application is required for the following items:

- a.	Retaining walls or block fence walls

- b.	Grading work

- c.	Swimming pools

- d.	Separate structures

- e.	Shoring

- f.	Demolition

- g.	Electrical, Mechanical, and/or Plumbing work

- h.	Fire sprinkler systems

- i.	Signs

- j.	Others_________________________________

- When all required approvals are obtained, the permit application must be signed by the property owner, licensed contractor, or authorized agent at the time the permit is to be issued:

- a.	For owner-builder permits: Owner’s signature can be verified with owner’s driver license. Owner’s representatives must present owner’s approval with a notarized letter from the owner.

- b.	For contractor building permits: Prior to the issuance of a building permit, the contractor shall have the following:

- i.	Certificate of workers Compensation Insurance made out to the Contractors State License Board.

- ii.	Copy of Contractors State License or pocket ID.

- iii.	Copy of city business tax registration certificate or a newly paid receipt for one.

- iv.	Notarized letter of authorization for agents.

- B.	ADMINISTRATION

- Obtain all approvals/clearances from the following department/bureau/agency noted below. It is necessary to apply immediately for the signoff as it can take weeks or months for some departments/bureaus/agencies to review and approve the project. All required approvals/clearances must be secured prior to permit issuance.

- The final set of construction documents must be stamped by the following department/bureau/agency:

- a.	Planning

- b.	Fire

- c.	Public Works

- d.	Health

- e.	Others_________________________________

- Each sheet of the construction documents must bear the signatures, registration number and expiration date of the registered design professional in responsible charge licensed in the State of California.

- The address of the project and the name/address of the owner are required on the first sheet or title sheet of the construction documents. Include the name/address of the registered design professionals and/or consultants on the construction documents where applicable.

- _____ set(s) of construction documents will be required during permit issuance. Construction documents must be:

- a.	Quality blue or black line drawings with uniform and light background color.

- b.	Max. 36' x 48" size with min. 1/8" lettering size.

- c.	Sticky back details must produce prints without contrasting shades of background color.

- Provide the following type of information with each set of construction documents:

- a.	Topography Survey Map

- b.	Grading

- c.	Floor Plans

- d.	Two Elevations

- e.	Construction Sections

- f.	Foundation Plans

- h.	Framing Plans

- i.	Structural Details

- j.	Others_________________________________

- Show the building area, occupancy group(s), use(s), type of construction(s), number of story(ies), height, type of fire sprinklers system provided, and the number of parking space(s) on the first sheet or title sheet of the construction documents. Include justification and analysis for increase in area, height, and/or story.

- Show on site plans the natural and finish grade elevations around the perimeter of the building. Show elevations for all floors and top of roof. Survey map signed by a licensed Surveyor or Civil Engineer may be required by the department.

- Remove all plans, details or notes that do not pertain to the project.

- CHAPTER 3 USE AND OCCUPANCY

- C.	USE AND OCCUPANCY

- Specify on floor plans uses of all rooms or areas.

- The occupancy group specified for one or more areas within the building is incorrect. See plan check annotation on sheet ___________.

- One or more occupancy has been incorrectly categorized. Change occupancy designation as identified below:

- a.	A-2 occupancy. Restaurants, bars, eating & drinking establishments with ≥ 50 occupants

- b.	A-3 occupancy., halls & recreational assembly or “other assembly”

- c.	B occupancy.

- Business type uses,

- Assembly rooms and spaces accessory to another use, with < 50 occupants,

- Tenant spaces and buildings used for assembly use with <50 occupants,

- Outpatient clinics not classified as Group I-2.1

- d.	M occupancy. Mercantile

- e.	R-1 occupancy. Hotels and motels (transient) with < 30 day duration

- f.	R-2 occupancy. Apartments, condominiums, extended-stay hotels with ≥ 30 day duration

- g.	S-1 occupancy. Moderate hazard storage

- h.	S-2 occupancy. Low hazard storage

- S-2 occupancy.  Parking garages

- i.	U occupancy. Utility and miscellaneous structures

- j.	_____ occupancy.

- CHAPTER 4 SPECIAL DETAILED REQUIREMENTS

- D.	GROUP R USES

- Group R-1 and R-2 dwelling requirements shall comply with CBC 420.

- Separation between individual dwelling units shall be a min. of 1-hr. fire partitions, except for fully sprinklered Type IIB, IIIB or VB buildings which may be reduced to 1/2-hr. fire partitions. (CBC 709.3)

- Separation between individual dwelling units shall be a min. of 1-hr. fire partitions, except for fully sprinklered Type IIB, IIIB or VB buildings which may be reduced to 1/2-hr. fire partitions. (CBC 709.3)

- E.	OTHER USE AND OCCUPANCY

- High-rise buildings shall comply with CBC 403.

- a.	Provide note on plans that a sprinkler water-flow alarm-initiating device and control valve with a supervisory signal-initiating device shall be installed at the lateral connection to the riser at each floor. It shall be the applicant’s responsibility to coordinate this requirement with the fire sprinkler design consultant. (CBC 403.3)

- b.	A lobby is required for each elevator in accordance with CBC 713.14.1

- c.	Provide note on plans that a smoke control system shall be installed. It shall be the applicant’s responsibility to coordinate this requirement with the mechanical/ventilation consultant.  (403.4.7.1)

- d.	Exit enclosures require specific smoke protection as required by CBC 909.20 and 1022.10.

- Motor-vehicle related occupancies shall comply with CBC 406.

  - Provide a min. 2’-9” high vehicle barrier at all floor-elevation differentials greater than 1-foot. (CBC 406.4.3)

  - Vehicle ramps may not serve as exits unless a pedestrian path is also provided. Show dedicated area that will serve as the pedestrian path that is not part of the vehicle ramp. (CBC 406.4.4)

  - Vehicle ramps used for parking shall have a max. slope of 1:15. (CBC 406.4.4)

  - Except for Group S-2 parking garages, slope all parking surfaces to a drain or the vehicle entrance. (CBC 406.4.5)

  - Open parking garages shall be of Type I, II or IV construction. (CBC 406.5.1)

  - Carports shall be open on no fewer than two sides.  The proposed structure is a garage. (406.3.3)

- The _______________ (use) (building) (occupancy) shall comply with CBC Section __________.

- CHAPTER 5 GENERAL BUILDING HEIGHTS AND AREAS

- F.	HEIGHTS AND AREAS

- On site plan, dimension distances from building(s) to all property lines, street center lines, and adjacent existing or proposed structures on the site.

- On site plan show all interior assumed lot lines, any designated flood plains, open space easements or development restricted areas.

- Show the size, use, occupancy, and type of construction of all existing buildings on the site.

- Clearly show the max. height of the building as defined in CBC Chapter 2.

- Clearly show if the lower level is a basement based on the definitions in CBC Chapter 2.

- On title sheet, show justification to exceed the basic allowable floor area listed in CBC T-503.

- On title sheet, show justification to exceed the number of stories or building height listed in CBC T-503.

- Provide calculations to justify increase in allowable area

- When a new building is constructed adjacent to an existing building, show the required wall and opening protection requirements for the existing building will be maintained. CBC 503.1.2, T-508.4, CBC 705.3, and T-705.8.

- Identify “Grade Plane” elevation for this project. Show the grade plane reference datum on all elevation and section drawings.

- Justify the assumed grade plane for this project pursuant to CBC Chapter 2. Grade plane is determined as the average elevation of the lowest points around the perimeter of the building within the space.

- For R-2 occupancy apartments and condominiums of Type VA construction using the sprinkler system increase for height shall not 60’ or 4 stories. (CBC 504.2)

- Provide a note on plans that the automatic sprinkler system must comply with the provisions of CBC 903.3.1.1 (NFPA-13) in order to achieve an increase in (height) (area). It shall be the applicant’s responsibility to coordinate this requirement with the sprinkler design consultant.

- When sprinkler increases are applied for an additional 20’ in height or for an additional story in accordance with CBC 504.2, sprinklers may not be used for an area increase in CBC 506.3 for Group A, E, H, I, L, Occupancies and high-rises. Pursuant to CBC 506.3, an automatic sprinkler system may be used for either an area increase or a height increase, but not both.

- Justify the multiple-story increase in the allowable area for the building. The building contains one or more of the following Group occupancies: A, E, H, I, L, or R or is a high-rise building. Therefore, the allowable area for the building may only be doubled, and shall not be tripled. (CBC 506.4)

- On site plan, clearly delineate any frontage used to for allowable area increases per CBC 506.2.

- Justify area frontage increase factor (If). Ratio of W/30 shall be limited to a value of 1.0 unless the building meets the requirements for unlimited area except for the 60’ wide yards, pursuant to CBC 507. (CBC 506.2.1)

- Note on plans: “Frontage used for allowable area increases per CBC 506.2 shall be permanently maintained”.

- The area increases per CBC 506.3 shall not apply where fire rating substitution of CBC T-601, Note d is used.

- For buildings equipped with an NFPA 13R or 13D sprinkler system, the area increases per CBC 506.3 do not apply.

- Unless considered a separate story, the floor area of a mezzanine shall be considered a part of the story in which it is located. The mezzanine area shall not contribute to either the building area or number of stories. (CBC 505.2)

- G.	MIXED OCCUPANCY

- Where mixed occupancy buildings contain incidental use areas, the following shall apply:

- a.	Clearly identify on plans whether there are any incidental accessory occupancies that are separated from other portions of the building pursuant to CBC T-509.

- b.	The protection used for incidental use areas may include automatic fire sprinklers, fire-resistance rated construction, or both. Identify such protection in the incidental use areas on each floor plan.

- c.	When CBC T-509 allows incidental uses to be protected by an automatic fire sprinkler system without the construction of a fire-resistance rated wall or floor ceiling assembly, such area shall be separated from the remainder of the building by construction capable of resisting the passage of smoke such as a smoke barrier or smoke partition. (CBC 509.4.2)

- Where mixed occupancy buildings contain non-separated uses, the following shall apply:

- a.	Clearly identify on plans whether non-separated uses will be utilized pursuant to CBC 508.3.

- b.	The adjoining non-separated uses must be clearly identified on all floor plans, including the boundary of such areas

- c.	The project must be designed to meet the requirements of the more restrictive occupancy for area and height.

- Where mixed occupancy buildings contain separated uses, the following shall apply:

  - Clearly identify on plans the boundary of each adjoining occupancy that will be separated pursuant to CBC 508.4 and T-508.4

  - Fire-resistance rated walls used to separate adjoining occupancies shall be constructed as fire barriers; fire partitions shall not be allowed. (CBC 508.4.4.1)

  - Fire-resistance rated floor-ceiling assemblies used to separate adjoining occupancies shall comply with CBC 711. (CBC 508.4.4.1)

- Where mixed occupancy buildings contain accessory areas, the aggregate area of all accessory areas within a single occupancy shall not exceed 10% of the floor area of the primary occupancy. (CBC 508.2.1)

- For buildings with mixed occupancies, the allowable area per story shall be based on the most restrictive provisions for each occupancy when the mixed occupancies are treated according to CBC 508.3 (unseparated). If treated per CBC 508.4 (separated) the max. total building area shall be such that the sum of the ratios for each of the actual area to allowable area does not exceed 1 for each story.

CHAPTER 6 TYPES OF CONSTRUCTION

H.	TYPES OF CONSTRUCTION

- Exterior walls shall have a fire-resistance rating not less than that specified in CBC T-601 and T-602. Provide details of its construction.

- Structural elements in exterior walls required to be of fire-resistance-rated construction shall have fire-resistance rating equal to or greater than that required for an exterior bearing wall. (CBC T-602)

- Provide details, notes and specifications for the fire protection of building elements as required for the type of construction. (CBC T-601 and CBC 602)

CHAPTER 7 FIRE-RESISTANCE-RATED CONSTRUCTION

I.	EXTERIOR WALLS

- Projections located where openings are required to be protected shall be non-combustible, heavy timber, or 1-hr. construction. (CBC 705.2)

- Projections beyond the exterior wall shall not extend beyond (clearly show on elevations/cross section):

  - A point one-third the distance from the exterior face of the wall to the lot line  where protected openings are required or a combination of protected and unprotected are required. (CBC 705.2)

  - Where all openings are allowed to be unprotected or the building is fully sprinklered per Section 705.8.2, a point one-half the distance from the exterior face of the wall to the lot line

  - More than 12” into areas where openings are prohibited. (CBC 704.2)

(Buildings on the same lot and considered as portions of one building per Section 705.3 are exempt from these provisions.)

- When two or more buildings are on the same property and they are not analyzed to comply as one building, the buildings shall have an assumed property line between them for determining wall and opening protection requirements or treated as a single building per CBC 705.3.

- When a new building is constructed adjacent to an existing building, an assumed property line shall be placed between them at any point such that the wall and opening protection requirements for the existing building will be maintained. (CBC 503.1.2, T-508.4, T-705.8 and 705.3)

(Buildings on the same lot and considered as portions of one building per Section 705.3 are exempt from these provisions.)

- The fire resistance rating of exterior walls shall comply with the provisions of CBC 705.5.

- The max. area of exterior wall openings in any story shall not exceed that allowed in CBC T-705.8.

- Where both unprotected and protected openings are permitted, the total area is limited to Eq. 7-2. (CBC 705.8, T-705.8)

- Exterior wall with a fire separation distance of ____ ft. or less shall be provided with a parapet not less than 30” height above roof (see 705.11 for exception). (CBC 705.11, T-705.8)

- Parapets shall have the same fire-resistance rating as the wall supporting them. The uppermost 18” of the parapet wall facing the roof shall be of noncombustible face materials. (CBC 705.11.1)

- Openings in exterior walls required to have protected openings shall have fire protection rating of (3/4) (1-1/2) hour assemblies. (CBC 705.8.2, T-716.5, T-716.6)

- Fire rated door vision panel size is limited to 100sq.in./ maximum size tested. (T-716.5)

J.	INTERIOR WALLS

- Clearly label and identify on plans fire walls, fire barriers, fire partitions, shafts, smoke barriers, and smoke partitions, along with their fire-resistance ratings.

- On site plan and floor plans, clearly show location of all fire walls as defined in CBC 706.

- Provide details to show that fire wall complies with CBC 706 including but not limited to:

a.	Fire rating shall be ____-hour per CBC T-706.4

b.	Fire walls must remain structurally stable in the event of collapse of construction on either side during a fire. Provide a detail to show that joist supported by the fire wall is spliced and not continuous (plywood membrane may be continuous), or provide double fire walls or provide justification for any other method used. 706.2

c.	Shall be noncombustible material, except in Type V Construction per CBC 706.3

d.	Shall have horizontal continuity per CBC 706.5

e.	Shall extend vertically from the foundation to a point 30” above the roof per CBC 706.6 (see exceptions).

f.	The area of each opening in fire walls is limited to 156 sq. ft. Total width of the openings is limited to 25% of the wall length in the story under consideration. The area can be more than       156 sq.ft., if both portions of the building are sprinklered per 903.3.1.1(706.8)

g.	All openings in fire walls shall be protected with fire assemblies having a fire-resistance rating of (1-1/2) (3) hours. (CBC T-715.4)

h.	Ducts and air transfer openings through fire walls should be avoided. If allowed, duct and air transfer opening penetrations shall be protected as required in CBC 717. Dampers are required. (CBC 706.11)

i.	Exits must be provided independently for each area bounded by fire walls except for horizontal exits per CBC 1025.

- No openings are allowed in the party wall per 706.1.1 when a wall is constructed on or near a property line.

- Fire walls terminating at exterior walls must comply with CBC 706.5.1.

- Combustible members framed into hollow fire walls or fire walls of hollow units, hollow spaces shall be solidly filled for the full thickness of the wall and for a distance not less than 4” above, below and between the structural members, with noncombustible materials approved for fireblocking. (CBC 706.7)

- A complete ____-hour separation is required between Group ________ and Group ________ occupancies. Occupancy separation walls shall to be fire barriers complying with CBC 707. Horizontal assemblies shall comply with CBC 711. Openings in the separation shall have ____-hour fire assemblies. (CBC 508.4, T-508.4, 707, 711, and 716)

- Fire barriers and horizontal assemblies separating single occupancies into different fire areas shall be ____-hour fire rated per CBC T-707.3.10

- Areas of each opening in fire barrier are limited 156 sq. ft. Total width is limited to 25% of the wall length in the story under consideration. (CBC 707.6)

- Fire barrier continuity must be detailed in accordance with 707.5 CBC.

- Fire barrier at vertical occupancy separations must have continuity and must extend through under-floor area, attic areas, and suspended ceiling areas (707.5)

- Openings in a fire barrier shall be protected in accordance with CBC 716, limited to a max. aggregate width of 25% and no opening shall exceed 156 sq. ft. (CBC 707.6)

- Provide a fire barrier in accordance with CBC 707 for the:

a.	Shaft enclosure per CBC 713.4.

b.	Exit enclosure per CBC 1022.1.

c.	Exit passageway per CBC 1023.3.

d.	Horizontal exit per CBC 1025.1.

e.	Atrium per CBC 404.6.

f.	Incidental accessory occupancy at the __________________ per T-509.

g.	Control areas per CBC 414.2.4.

h.	Occupancy separation per CBC 508.4.

i.	Fire area separation per CBC 707.3.10.

- Provide ____-hour fire rated door assemblies in ____-hour fire barrier. (CBC 707.6 and T-716.5)

- All structural elements supporting a fire barrier must have the same fire-resistance ratings as the required occupancy separation. (CBC 707.5.1)

- Provide a fire partition in accordance with CBC 708.1 for:

a.	Walls separating dwelling units in the same building.

b.	Walls separating sleeping units in the same building.

c.	Corridor walls, as required per section 1018.1.

d.	Elevator lobby per CBC 713.14.1.

- Fire partition continuity must be detailed in accordance with CBC 708.4.

- Smoke barriers are required and shall have a min. 1-hr. fire-resistance rating. (CBC 709.3)

- Smoke barriers shall from an effective continuous barrier per the requirements of CBC 709.4.

- Smoke partitions shall comply with the requirements of CBC 710.

- Floor and roof assemblies required to have fire-resistance rating shall comply with the requirements of CBC 711.

- In 1-hr. fire-resistance-rated horizontal assemblies where unusable space occurs above or below the assembly, the membrane on the unusable side of the assembly is not required to be installed. CBC 711.3.3

- Penetrations of fire-resistance-rated construction must comply with CBC 714.

- In fire-resistance-rated walls, detail through penetrations and membrane penetrations per CBC 714.3.1 and 714.3.2.

- Penetrations in fire-resistance-rated walls shall comply with CBC 714.3. Through penetrations shall comply with CBC 714.3.1.1 or 714.3.1.2, or as noted below: (CBC 714.3.1)

  - Steel, ferrous or copper pipes may penetrate fire-resistance rated walls, provided the opening is protected as follows: (CBC 713.4.1 EX.)

    - Item penetrating concrete or masonry walls is a max. 6” nominal diameter and the area of the opening through the wall does not exceed 144 sq. in., concrete, grout or mortar is permitted where it is installed the full thickness of the wall or the thickness required to maintain the fire-resistance rating; or

    - When the annular space is protected with material that meets ASTM E 119 or UL 263.

  - Penetrations shall be fire-stopped by a system installed as tested in accordance with ASTM E 814 or UL 1479, and shall have an F rating of not less than the required fire-resistance-rating of the wall penetrated. (CBC 714.3.1.2)

  - Membrane penetrations of max. 2-hr. fire-resistance rated walls by steel electrical boxes are permitted, provided that each does not exceed 16 sq. in. in area and the total area of such openings does not exceed 100 sq. in. for any 100 sq. ft. of wall area, and the space between the wall membrane and the box does not exceed 1/8”. Additionally, outlet boxes on opposite sides of the wall shall be separated by a horizontal distance of not less than 24” or other listed method. (CBC 714.3.2 EX. 1)

  - Membrane penetrations by listed electrical boxes of any material are permitted, provided such boxes have been tested for use in fire-resistance-rated assemblies, and the space between the wall membrane and the box does not exceed 1/8” unless listed otherwise. Additionally, outlet boxes on opposite sides of the wall shall be separated by a horizontal distance of not less than 24” or other listed method. (CBC 714.3.2 EX. 2)

  - Membrane penetrations by electrical boxes of any size or type,, which have been listed as part of a wall opening protective material system for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. (CBC 714.3.2, EX 3)

  - Membrane penetrations by boxes other than electrical boxes, provided such penetrating items and the annular space between the wall membrane and the box, are protected by an approved membrane penetration firestop system in accordance with ASTM E814 or UL 1479 4 (CBC 714.3.2, EX 4).

  - A fire sprinkler shall be permitted to be unprotected provided such space is covered by a metal escutcheon plate. (CBC 712.3.2 EX. 5)

  - Where walls are penetrated by other materials or openings larger than those mentioned above, they must be qualified by tests in accordance with CBC 703.3.

- In fire-resistance-rated horizontal assemblies, detail through penetrations and membrane penetrations per CBC 714.4.

- Penetrations of fire-resistance-rated horizontal assemblies shall comply with CBC 714.4. Through penetrations shall comply with CBC 714.4.1.1.1 or 714.4.1.1.2, or as noted below: (CBC 714.4.1.1)

  - Steel, ferrous or copper conduits may penetrate a single fire-resistance-rated floor assembly when the annular space is protected with material that meets ASTM E 119 or UL 263 per CBC 714.4.1.1 EX. 1

  - Penetrating items, as noted above, with a max. 6” nominal diameter shall not be limited to the penetration of a single fire-resistance rated floor assembly, provided that the area of the openings does not exceed 144 sq.in.in any 100 sq.ft. of floor area.(CBC 714.4.1.1 EX.1)

  - Membrane penetrations by listed electrical outlet boxes are permitted provided such boxes have been tested for use in fire-resistance-rated assemblies, and the space between the ceiling membrane and the box does not exceed 1/8” unless listed otherwise. (CBC 714.4.1.2 EX. 3)

- Joints installed in or between fire-resistance-rated walls, floor or floor/ceiling assemblies and roofs or roof/ceiling assemblies shall be protected an approved fire-resistant joint system with a fire-resistance rating not less than that of the assembly in which it is installed. Provide details. (CBC 715.1)

- Fire-resistance-rated assemblies shall be supported with a structural system having an equivalent fire-resistance-rated protection. (CBC 704.1)

- Where columns are required to be fire-resistance rated, the entire column, including its connections, shall be protected. (CBC 704.2)

- Primary structural frame members, other than columns, required to have a fire-resistance-rating supporting more than two floors or one floor and roof, or support a load-bearing wall or a non-load-bearing wall more than two stories high are required to have individual encasement protection. (CBC 704.3)

- Where the fire protective covering of a structural member is subject to impact damage from moving vehicles, the handling of merchandise or other activity, the fire protective covering shall be protected by corner guards or by a substantial jacket of metal or other noncombustible material to a height adequate to provide full protection, but not less than 5’ from the finished floor. (CBC 704.9)

- Fire door assemblies shall be listed for the intended purpose and use. (CBC 716.4.3.1)

- Fire- rated glazing assemblies shall be marked in accordance with Tables 716.3, 716.5 and 716.6. (CBC 716.3)

- Fire doors and fire-protection rated glazing shall bear labels as required by CBC 716.5.6.

- Fire dampers shall have the min. fire protection rating specified in CBC T-717.3.2.1 for the type of penetration. (CBC 717.3.2)

- Fire dampers, smoke dampers, combination fire/smoke dampers and ceiling radiation dampers shall be provided as prescribed in CBC 717.5.1 through 717.5.7 and CBC 717.6.

- Fireblocking shall be installed in combustible concealed locations in accordance with CBC 718.2 in the following locations: (Provide Details)

              - In concealed spaces of stud walls and partitions, including furred spaces and parallel rows of studs or staggered studs, as follows:

                - Vertically at the ceiling and floor levels.

                - Horizontally at intervals not exceeding 10’. (CBC 718.2.2)

              - At all interconnections between concealed vertical stud wall or partition spaces and concealed horizontal spaces created by an assembly of floor joists or trusses, and between concealed vertical and horizontal spaces such as occur at soffits, drop ceilings, cove ceilings and similar locations. (CBC 718.2.3)

  - In concealed spaces between stair stringers at the top and bottom of the run. Enclosed spaces under stairs shall also comply with CBC 1009.9.3.

  - Where annular space protection is provided in accordance with CBC 712.1.7, Exception 1 of CBC 714.4.1.2,  or CBC 714.4.2, fireblocking shall be installed at openings around vents, pipes, ducts, chimneys and fireplaces with an approved material to resist the free passage of flame and the products of combustion. (CBC 718.2.5)

- Draftstopping shall be installed in combustible concealed locations in accordance with CBC 718.3 and 718.4, respectively, at the following locations: (Provide Details)

  - Above and in line with dwelling unit and sleeping unit separations. (CBC 718.3.2)

  - In attics and concealed roof spaces above and in line with sleeping unit and dwelling unit separations that do not extend to the underside of the roof sheathing above. (CBC 718.4.2)

  - Show draft-stop construction on the plans. Draftstopping materials shall not be less than 1/2” gypsum board, 3/8” wood structural panel, 3/8” particleboard, 1” nominal lumber, cement fiberboard, batts or blankets of mineral wool or glass fiber, or other approved materials adequately supported. (CBC 718.3.1)

  - Openings in the attic partitions shall be protected by self-closing doors with automatic latches constructed as required for the partitions. (CBC 718.4.1.1)

- CHAPTER 8 INTERIOR FINISHES

- K.	INTERIOR FINISHES

- Where finish materials are applied on walls, ceilings or structural elements required to have a fire-resistance rating or to be of noncombustible construction, they shall comply with the requirements of CBC 803.

(If mixed uses are provided, then use Table 803.9 for interior wall and ceiling requirements)

- Note on plans or finish schedule: “Wall, floor and ceiling finishes shall not exceed the flame spread classifications in CBC T-803.9".

- Interior floor finish and floor covering materials shall comply with CBC 804.

- Combustible materials installed on or embedded in floors of buildings of Type I or II construction shall comply with CBC 805.1.1 through 805.1.3.

- Decorative materials and trim installed in buildings governed by the SFM shall comply with the provisions of CBC 806.

- CHAPTER 9 FIRE PROTECTION SYSTEMS

- L.	FIRE PROTECTION SYSTEM

- Fire barriers separating fire areas shall be rated in accordance with CBC 707.3.10. (CBC 901.7)

- An automatic sprinkler system is required throughout all buildings with a Group “R” fire area. (CBC 903.2.8)

- Exceptions to, or reductions in building code requirements based on the installation of automatic fire extinguishing system is not allowed when utilizing NFPA-13R type residential sprinkler system allowed for Group “R” occupancies. (CBC 903.2.8, 903.3.1.2, 504.2, 506.3, & T-601).

- An approved automatic sprinkler system is required throughout the (entire building) (fire area) where the (building) (fire area) contains the following: (CBC 903.2)

- a.	Has a(n) _____ occupancy; and/or

- b.	Has a fire area over __________ sq. ft.; and/or

- c.	Has over _____ occupant load.

- d.	____________________________.

- Building with floor areas over 1,500 sq. ft. shall be sprinklered where 20 sq. ft. of opening for every 50 ft of exterior wall length is not provided on at least one side. (CBC 903.2.11.1)

- Provide automatic sprinkler system at top of rubbish and linen chutes and in their terminal room. Chutes shall have additional sprinkler heads installed at alternate floors and at the lowest intake.  Chutes shall be accessible for servicing.  (CBC 903.2.11.2)

- Add a note on plan: “This building must be equipped with an automatic fire extinguishing system complying with (NFPA-13) (NFPA-13R). The sprinkler system shall be approved by _______________ prior to installation.” (CBC 903.3.1)

- Class (I) (II) (III) standpipe (dry) (wet) (combination) systems are required in this building. Show the location of standpipe hose connections on the plans. (CBC 905.3 & 905.4)

- A (manual) (automatic) fire alarm system is required as a condition for the _____ occupancy. (CBC 907.2)

- Group R occupancies with smoke alarm systems, hard-wired smoke detectors with a battery back up, shall be provided in the following areas (show location on the plans): (CBC 907.2.11 & 907.2.11.5)

- a.	Group R-1: sleeping areas, in every room in the path of egress from the sleeping room to the exit door, in each story within the sleeping unit, in enclosed common stairwells.

- b.	Groups R-2, R-3, R-3.1, R-4, and I-1: on the ceiling or wall outside of all sleeping areas, in each room used for sleeping purposes, in each story within a dwelling unit, in enclosed common stairwells, in Group R-3.1 in addition to the above throughout the habitable areas except the kitchen.

- c.	Power source shall be from the building wiring and shall be equipped with battery backup.

- CHAPTER 10 MEANS OF EGRESS

- (Please refer to separate checklist for accessibility issues if applicable)

- M.	EXITS

- Submit an exit plan that labels and clearly shows compliance with all required egress features such as, but not limited to, common path of travel, required number of exits, occupant load, required width, continuity, travel distance, etc. (CBC 1001.1)

- In a multi-story, Group R-2 building, two exits or more are required when the number of dwelling units exceeds 4 or, travel distance to an exit exceeds 50’. (CBC 1021.1, CBC T-1021.2(1))

- The number of exits shall comply with CBC T-1015.1, T-1021.3.1, T-1021.2(1) and T-1021.2 (2).

- Rooms with a common path of egress travel exceeding that allowed in CBC 1014.3 shall have two separate and distinct means of egress.

- When two exits are required from a building or area, they shall be separated by one-half (one-third if sprinklered throughout) the diagonal dimension of the building or area served. (CBC 1015.2.1)

- Exit width shall be not less than permitted by CBC 1005. The net dimension (clear width) shall be used in determining exit width.

- In single-story buildings, two or more exits are required when criteria in CBC T-1015.1, T-1016.2, T-1021.2(1) or or T-1021.2(2) are exceeded. (CBC 1015, 1016, & 1021)

- Travel distance to reach an exit shall not exceed that allowed in CBC T-1016.2.

- Every room or space that is assembly occupancy shall have the occupant load posted in a conspicuous place near the main exit of the room. (CBC 1004.3)

- N.	CORRIDORS

  - Corridor and exit balcony widths shall be not less than (24”) (36”) (44”) (72”) (96”) at the following locations: _____________________. (CBC 1018.2)

  - Dead ends in 1-hr corridors shall not exceed 20’ (50’) in length based on use at the following locations _____. (CBC 1018.4)

  - Provide a complete architectural section of 1-hr. corridor detailing fire-resistance-rated construction of the walls and ceilings. Detail all duct and other penetrations. (CBC 708.4, 1018.1, 716.1, T-716.5 & 717.5.4)

  - Provide fire/smoke dampers at duct penetrations of  1-hr corridor walls. (CBC 717.5.4.1)

  - Glazed openings into 1-hr. corridors shall be protected per CBC T-716.5. The total area of such openings shall not exceed 25% of the common wall with any room per CBC 716.6.7.2.

  - Corridor walls may terminate at the ceiling, only if the entire ceiling is an element of 1-hr. floor or roof assembly. (CBC 708.4)

  - 1-hr. corridors and any enclosed ceilings within them shall not be used as an integral part of the duct system. (CBC 1018.5)

  - At rooms with exhaust fans adjacent to 1-hr corridors, show how make up air is provided. No louvers shall be provided. (CBC 1018.5 & 716.5.3.1)

- O.	DOORS

- Provide specifications for the door hardware (i.e., lever type, push-pull, panic, etc.) to comply with disabled access requirements.

- Except within individual dwelling units, doors opening into the path of egress travel shall not reduce the required width to less than one half during the course of swing. When fully open, the door shall not project more than 7” into the required width. (CBC 1005.7.1)

- Each leaf of door in the means of egress shall provide 32” clear opening and a min. height of 6’-8”, but in no case shall any swinging door leaf exceed 48”. (CBC 1008.1.1)

- When additional doors are provided, they shall conform to the provisions for exit doors. (CBC 1008.1)

- Doors serving an occupant load of 50 or more shall swing in the direction of exit travel CBC 1008.1.2.

- Revolving, sliding or overhead doors shall not be used as exit doors, unless they comply with CBC 1008.1.4. (CBC 1008.1.2)

- Show that power operated doors are capable of being manually opened to permit exit travel in the event of a power failure. (CBC 1008.1.4.2)

- Door swinging over landing shall not reduce the width by more than 7” when fully open. When serving 50 or more, the door in any position shall not reduce the required width to less than one-half. (CBC 1008.1.6)

- Thresholds at doorways shall not exceed 1/2” in height above the finished floor or landing. Raised thresholds and floor level changes greater than 1/4” at doorways shall be beveled with a slope not greater than one unit vertical in two units horizontal. (CBC 1008.1.7)

- All exit doors and gates from an ________ occupancy shall not be provided with a latch or lock, unless it is panic hardware. (CBC 1008.1.9)

- Fire rated doors shall be installed in accordance with NFPA 80.

- Fore fire rated doors, dead bolts cannot be used, unless they are interconnected with latch bolds and retract when the latch bolt is retracted.  (1008.1.9 and NFPA 80)

- Doors and their frames opening into a 1-hr. corridor shall be labeled 20-minute smoke and draft control assemblies with self or automatic closers. (CBC 716.5.3 & 716.5.7.3)

- Two exits or exit access doors of egress shall be provided from boiler, incinerator, or furnace rooms which exceed 500 sq. ft. and any fuel fired equipment exceeding 400,000 Btu input capacity. One exit is permitted to be a fixed ladder or alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the max. horizontal dimension of room. (CBC 1015.3).

- P.	STAIRWAYS

- Stairs shall have a min. width of (44”) (36”) at the following locations ______. (CBC 1009.4)

- Within individual dwelling residential dwelling units, stairways shall be detailed as follows:

- a.	Max 7.75” and min. 4” riser height. (CBC 1009.7.2)

- b.	Min. 10” tread depth. (CBC 1009.7.2)

- c.	Min. 36” clear width. (CBC 1009.4)

- d.	Min. 6’-8” vertical headroom measured vertically from a line connecting the edge of the nosing. (CBC 1009.5)

- In common areas or in non-residential areas, provide sections and details of interior or exterior stairways showing:

- a.	Max. tread rise of 7” (min. 4”) and min. tread run of 11”. (CBC 1009.7.2)

- b.	Min. headroom of 6’-8”. (CBC 1009.5)

- c.	Enclosed usable space under stairways require 1-hr. construction on enclosed side. (CBC 1009.9.3)

- Curved stairways with winders shall have treads and rises in accordance with CBC 1009.7 and the smallest radius shall not be less than twice the required width of the stairway. (CBC 1009.11)

- Submit shop drawings for spiral stairway showing compliance with CBC 1009.12. Spiral stairways shall be detailed as follows:

- a.	Min. 7.5” clear tread depth at a point 12” from the narrow edge.

- b.	Min. 6’-6” vertical headroom measured vertically from a line connecting the edge of the nosing.

- c.	Max. 9.5” riser height.

- d.	Min. 26” stairway width.

- Provide a barrier from upper stairs, and stairs leading to the basement. (CBC 1022.8)

- Stairs shall be enclosed with fire barriers per CBC 1022.2 at the following locations _____. Enclosures shall conform to the following:

  - 2-hr. fire-resistance-rated construction in all buildings 4 or more stories in height, and 1-hr. for all other buildings less than 4 stories.

  - Doors opening into exit enclosures shall be protected per CBC 716.

  - Exit enclosures shall include an exit passageway of the same fire-resistance-rated construction as the enclosure leading to the outside of the building, including openings.

  - Useable space is not allowed under the stairs. (CBC 1009.9.3)

- Exterior stairs shall be separated from the interior of the building with the same fire-resistance-rated construction required for interior stairs. (CBC 1026.6)

- In buildings 4 or more stories:

- a.	One stair must extend to the roof. (CBC 1009.16)

- b.	Stairs must have a penthouse or a smoke hatch. (CBC 1009.16.1)

- Stairs in buildings over 75’ (55’ due to local ordinance which may apply) in height shall be in a smoke proof enclosure or pressurized stairway per CBC 909.20, 1022.10 and 202 high-rise definition.

- Except in fully sprinklered building per NFPA 13 or 13R, stairs leading from an area of refuges requires a min. of 48” clear between handrails. (CBC 1007.3)

- A min. of 2 areas of refuge with one at an elevator must be provided in accordance with CBC 1007.1, 1007.2.1, 1007.4 and 1007.6,  since the project is four or more stories above grade.

- Q.	OTHER COMPONENTS

- Handrails shall be detailed as follows: (CBC 1012)

- a.	Handrail shall be continuous without interruption. (CBC 1012.4)

- b.	Min. 34" to max. 38" high above the stair tread nosing. (CBC 1012.2)

- c.	Min. 1.25” to max. 2” (1-1/2” for accessibility) circular cross-section for handgrip portion of handrail. (CBC 1012.3)

- d.	Either a Type I or Type II handrail shall be used for non-circular handgrip portion of handrail. (CBC 1012.3)

- e.	Min. 0.01” radius for edge of handrail (i.e., no sharp corner). (CBC 1012.3)

- f.	Min. 12” horizontally extension beyond the top riser and continue to slope for the depth of one tread beyond the bottom riser serving more than one dwelling unit or not within a dwelling unit. (CBC 1012.6)

- g.	The handgrip shall extend 12” beyond the top and 12” plus tread width beyond bottom tread and return the handrail to newel post or wall. (See Title 24 Disabled Access for additional requirements).

- h.	Min. 1.5” clear space between handrail and wall. (CBC 1012.7)

- Guards shall be detailed as follows:

- a.	Guards shall be located along open-sided walking surfaces, mezzanines, stairways, ramps and landings that are more than 30” above the floor or grade below. (CBC 1013.1)

- b.	Guard whose top rail does not serve as a handrail shall have a height of 42” high above the leading edge of the tread. (CBC 1013.3)

- c.	Within individual dwelling units, a guard whose top rail serves as a handrail shall have a height of 34" to 38" high above the leading edge of the tread. (CBC 1013.3)

- d.	Within individual dwelling units, open guards along stairs shall not permit 4.375" diameter sphere to pass through any opening. (CBC 1013.4)

- e.	Triangular opening formed by tread, stair and bottom rail shall not permit 6” diameter sphere to pass through. (CBC 1013.4)

- Guards shall be provided where the roof hatch opening or mechanical equipment is located within 10’ of a roof edge or open side of a walking surface and such edge or open side is located more than 30” above the floor, roof or grade below. The guard shall be constructed so as to prevent the passage of a 21” diameter sphere. (CBC 1013.7)

- Provide emergency escape and rescue from sleeping rooms below the fourth story. Min. net clear opening dimensions of 24" height, 20" clear width, 5.7 sq. ft. area (5.0 sq. ft. at grade floor) and 44" max to bottom of clear opening is required. (CBC 1029)

- Provide window wells at emergency escape and rescue opening with sill height located below ground level. Min. area of 9 sq. ft., min. 3’ width, and provide fixed ladder for window wells with a max. vertical depth of 44”. (CBC 1029.5)

- Where elevation changes less than 12” occur in the means of egress, sloped surfaces shall be used. (CBC 1003.5)

- Ramp slopes shall not exceed the following:

a.	Max. 1’ in 12’ (8%) if part of egress. (CBC 1010.3)

b.	Max. 1’ in 8’ (12.5%) for all others. (CBC 1010.3)

c.	Max. 1’ in 48’ (2%) for cross slope. (CBC 1010.4)

d.	Max. 30” vertical rise. (CBC1010.5)

- Ramps with a rise greater than 6” shall have handrails on both sides. (CBC 1010.9)

- Where an egress court serving a building or portion thereof is less than 10’ in width, the egress court walls shall have not less than 1-hr. fire-resistance-rated construction for a distance of 10’ above the floor of the court. Openings within such walls shall be protected by opening protectives having a fire protection rating of not less than 3/4-hr.               (CBC  1026.6)

- Exterior balconies, stairways and ramps shall be located at least 10’ from adjacent lot lines and from other buildings on the same lot unless the adjacent building exterior walls and openings are protected in accordance with CBC 705 based on fire separation distance. (CBC 1026.5 and 1027.3)

- Balconies used for egress purposes shall conform to the same requirements as corridors for width, headroom, dead ends and projections. (CBC 1019)

- Exterior egress balconies shall be separated from the interior of the building by walls and opening protection as required by corridors. (CBC 1019.2)

- The means of egress system shall be illuminated with at least one foot candle at the floor level. (CBC 1006.2)

- Exit signs are required when 2 or more exits are required. Show location of all exit signs. (CBC 1011.1)

- Provide a separate source of power for exit sign illumination. (CBC 1011.6.3)

- Show conformance for floor-level exit signs and exit path marking in R-1 and R-2 occupancies per CBC 1011.7 and 1011.8 as enforced by the SFM.

- Show two sources of power for means of egress. (CBC 1006.3)

CHAPTER 11A & 11B ACCESSIBILITY REGULATIONS

See separate accessibility plan review checklist for Title 24, Part 2, of the California Building Code.

CHAPTER 12 INTERIOR ENVIRONMENT

R.	INTERIOR ROOM, LIGHT AND VENTILATION

- Provide a door and window schedule. Show type and size of each.

- Show the following dimensions for each room or area:

  - Habitable spaces shall not be less than 7’ in any plan dimension. (CBC 1208.1)

  - Occupiable spaces, habitable spaces, hallways & corridors shall have a ceiling height of no less than 7’-6”. (CBC 1208.2).

  - Bathrooms, toilet rooms, kitchens, storage rooms, & laundry rooms shall have a ceiling height of no less than 7’ (CBC 1208.2)

  - At least one room shall have a min. net area of 120 sq. ft. (CBC 1208.3)

  - Habitable areas shall have a min. net area of 70 sq. ft. (CBC 1208.3)

  - A kitchen area is not limited. (CBC 1208.3 EX 1)

- Provide natural ventilation in habitable rooms or bathrooms by means of openable exterior wall openings with an area not less than 4% of the room floor area. This is deficient in __________________. Mechanical ventilating systems may be permitted if designed in accordance with the Mechanical Code. (CBC 1203.4.1, CBC 1203.1)

- Provide natural ventilation for adjoining spaces. In order to consider any room as a portion of an adjoining room, the opening to the adjoining room shall be unobstructed and shall have an area of not less than 8% the floor area of the interior room or 25 sq. ft., whichever is greater. (CBC 1203.4.1.1)

- Where openings below grade provide required natural ventilation, the outside horizontal clear space measure perpendicular to the opening shall be 1-1/2 times the depth of the opening measured from adjoining ground level to the bottom of the opening. (CBC 1203.4.1.2)

- Rooms containing bathtubs, showers, spas and similar bathing fixtures shall be mechanically ventilated. Provide an exhaust fan with a min. capacity of 50 CFM. Ductless fans are unacceptable. (CBC 1203.4.2.1, CMC T-4-4)

- Provide natural light in habitable rooms by means of exterior glazed openings with an area not less than 8% of the room floor area. This is deficient in ______________________________. (CBC 1205.2)

- Provide natural light for adjoining spaces. In order to consider any room as a portion of an adjoining room, at least 1/2 of the common wall area shall be open and unobstructed and shall provide an opening of not less than 1/10 the floor area of the interior room or 25 sq. ft., whichever is greater. Show that the common wall between ______________ and _____________ complies. (CBC 1205.2.1)

- Openings required for natural light and ventilation shall be permitted to open into a thermally isolated sunroom or patios provided that:

a.	For natural light a glazed area of not less than 1/10 of the floor area of the interior room or 20 sq. ft., whichever is greater (1205.2.1 EX)

b.	For natural ventilation an area of not less than 8% of the floor area of the interior room or space, but not less than 20 sq. ft.. (1203.4.1.1 EX)

- Provide min. 1 foot-candle of stairway illumination at tread runs. (CBC 1205.4)

- For the purpose of providing natural light or ventilation at exterior openings of buildings, a min. yard of 3’ in width for one and two story building is required. For buildings more than two stories, the min. width of the yard shall be increased to 1 foot for each additional story. (CBC 1206.2)

- For the purpose of providing natural light or ventilation at exterior openings on opposite sides shall not be less than 6’ in width. Courts bounded on three or more sides by the wall of the buildings shall not be less than 10’ in length, unless bounded one end by a public way or yard. For buildings more than two stories in height, the court shall be increased 1 foot in width and 2’ in length for each additional story. (CBC 1206.3)

- Porch over required windows at _________________ must abut a public way, yard or court and have a min. clear height of 7’ with longer side at least 65% open and unobstructed. (CBC 1205.2.2 EX 1)

- All shower compartments, regardless of shape, shall have a min. finished interior area of not less than 1,024 sq. in. and shall be capable of encompassing a 30” circle. Shower doors shall swing out and be of safety glazing. The min. area and dimensions shall be maintained to a point 70” above the shower drain outlet. (CPC 411.7)

- Shower compartments and walls above bathtubs with installed shower heads shall be finished with a smooth and nonabsorbent surface to a height not less than 70” above the drain inlet per CBC 1210.3. Use of water-resistant gypsum backing board shall be per CBC 2509.2  and 2509.3.

- Built-in tubs with showers shall have waterproof joints between the tub and adjacent wall. (CBC 1210.4)

- Toilet rooms shall be provided with a fully openable exterior window with an area not less than 3 sq. ft. or a vertical duct not less than 100 sq. in. in area for the first water closet plus 50 sq. in. additional of area for each additional water closet, or a mechanically operated exhaust system capable of providing a complete change of air every 15 minutes. Such mechanically operated exhaust system shall be connected directly to the outside, and the point of discharge shall be at least 3’ from any opening that allows air entry into occupied portions of the building.

- Add the following notes to plans:

a.	Flush volumes for low-consumption and water-saver water closets shall be provided with a max. 1.6 gallons of water per flush (1.28 gal per flush 7/01/11). (CPC 402.1, 402.2)

b.	Water heater shall be strapped to wall at points within the upper 1/3 and lower 1/3 of its vertical dimensions with the lower a min. 4” above the controls. (CPC 508.2)

c.	Garage door extension springs shall be provided with an approved safety restraint device and  either hard drawn-spring wire or oil-tempered wire and installed in accordance with the manufacturer’s instruction. (CBC 1211)

d. Automatic garage door openers shall be equipped with rebound capability.  (CA Health and Safety Code 19890 and 19891)

- This plan contains _______________ courts. Provide details of the proposed wall construction, opening protection and stair protection. (CBC 202, 1206.3, 1203.4.3 and 1027.5)

- The width of courts shall meet the following: (CBC 1206.3)

a.	Not less than 3’ in width

b.	Not less than 6’ in width where openings occur on opposite sides

- Courts shall not be less than 10’ in length. (CBC 1206.3)

- Courts located in buildings more than 2-stories in height shall be shall be increased: (CBC 1206.3)

a.	1’ in width for each additional story

b.	2’ in length for each additional story

- Court access shall be provided at the bottom of courts. (CBC 1206.3.1)

- Courts more than 2-stories shall be provided with horizontal air intake at the bottom not less than 10 sq. ft. and leading to the exterior of the building. (CBC 1206.3.2)

- Courts shall be properly graded and drained to an approved drainage system. (CBC 1206.3.3)

- The ventilating area in enclosed attics and rafter spaces shall be as follows: (CBC 1203.2)

- a.	Show ventilation type, size, and location on the plans.

- b.	The net free ventilating area shall not be less 1/300 of the area of the space ventilated.

- c.	50% of the required ventilation area must be located at least 3’ above eave or cornice vents with the balance provided by eave or cornice vents.

- d.	Openings shall have corrosion-resistant wire mesh or other approved material with 1/8” min. and 1/4” max. opening.

- e.	A min. of 1” airspace shall be provided between insulation and roof sheathing.

- Provide min. 20” x 30” attic access opening where the attic has a clear height of over 30”. (CBC 1209.2)

- Under-floor vents shall meet the following requirements: (CBC 1203.3)

- a.	Show ventilation type, size, and location on the plans.

- b.	Openings shall be placed so as to provide cross ventilation of the under-floor space

- c.	The net free ventilating area shall not be less than 1/150 of the crawl-space area (approximately 10 sq. in. for each 10 sq. ft. of attic area).

- d.	Openings shall have corrosion-resistant wire mesh or other approved material with 1/8” min. and 1/4” max. opening.

- Show min. 18” x 24” under floor access opening. (CBC 1209.1)

- Access to mechanical appliances in under-floor areas, in attic spaces, and on roofs or elevated structures shall be in accordance with the California Mechanical Code. (CBC 1209.3)

- Sound Transmission. In Group R Occupancies, wall and floor- ceiling assemblies separating dwelling units or guest rooms from each other and from public space such as interior corridors and service areas shall provide airborne sound insulation for walls, and both airborne and impact sound insulation for floor-ceiling assemblies. All such separating walls and floor-ceiling assemblies shall provide an airborne sound insulation equal to that required to meet a sound transmission class (STC) of 50 per ASTM E 90 and E413 (45 if field tested). All separating floor-ceiling shall provide impact sound insulation equal to that required to meet an impact insulation class (IIC) of 50 oer ASTM E 492 and E 989 (45 if field tested). EXCEPTION: Impact sound insulation is not required for floor-ceiling assemblies over non habitable rooms or spaces not designed to be occupied, such as garages, mechanical rooms or storage areas. (CBC 1207.6.1, 1207.7 and 1207.8)

              - Identify all sound rated partitions on the floor plans.

              - Provide construction details for the following:

                - Sound rated wall assemblies.

                - Sound rated floor-ceiling assemblies.

              - Detail all penetrations or openings into sound rated partitions or approved permanent resilient sealants.

              - The entrance doors to residential units from interior corridors are required to have a min. STC rating of 26. (Laminated 1-3/8” solid-core doors with resilient stops and gaskets or 18 gauge insulated steel slab doors with compression seals all around, including thresholds will meet this requirement). (CBC 1207.7)

              - Field tests of corridor walls shall not include segments with doors.

              - Penetrations or openings in construction assemblies for piping, electrical devices, recessed cabinets, bathtubs, soffits or heating, ventilating or exhaust ducts shall be sealed, lined, insulated or otherwise treated to maintain the required ratings.

              - Floor covering may be included in the assembly to obtain the required rating.  These coverings must be retained as a permanent part of the assembly and may be replaced only by the other floor coverings that provide the required impact sound insulation.

- CHAPTER 14 EXTERIOR WALLS

- S.	EXTERIOR WALLS

- Provide veneer details. Show method of anchorage, size and spacing of anchors. Comply with the applicable requirements in CBC 1405.

- CHAPTER 15 ROOF ASSEMBLIES AND ROOFTOP STRUCTURES

- T.	ROOF

- The min. roof coverings installed on buildings shall comply with CBC T-1505.1 based on the type of construction of the building. Roof covering shall be Class C rated or better or as required. (CBC 1505.1)

- Provide specifications for roofing material and application on the plans. Identify the fire-retardant roof classification, manufacturer’s name, and ICC/UL/SFM report number. (CBC 1506.3)

- Specify approved weatherproof walking surface material at decks and balconies.

- Clay and concrete tile attachment shall comply with CBC T-1507.3.7.  Provide notes to show compliance. (CBC 1507.3.7)

- Provide minimum ___________ roof slope for ___________________ roof material. (CBC 1507)

- Built-up roofs shall have a min. slope of 1/4” per foot (2%) for drainage. (CBC 1507.10.1)

- Show roof slope(s), drain(s) and overflow drain(s) or scupper(s) on the roof plan. Provide a detail of the roof drain and overflow system. Roof drainage system shall comply with the following requirements: (CBC 1503.4, CPC 1108)

- a.	Size the roof drains and overflow drains in accordance with Chapter 11 of the CPC. (CBC 1503.4)

- b.	System shall be sized for min. rain intensity of 3” per hour.

- c.	The roof drain and overflow drain must maintain independent lines to the yard box.

- d.	Roof drainage is not permitted to flow over public property.

- e.	Secondary roof drains having the same size as the primary roof drains shall be installed with the inlet flow line located a min. 2” above the low point of the roof.

- f.	Scuppers through parapet walls adjacent to the low point of the roof may be used as secondary roof drainage. Scupper openings shall be a min. of 4” high and have a width equal to the circumference of the roof drain required for the area served.

- g.	Overflow scuppers shall be designed in accordance to CPC T-11-1.

- Provide and detail access to equipment on roof per CMC 904.10.3.

- Show that the penthouse and/or roof structures complies with the requirements of CBC 1509. (CBC 1509)

- For podium construction, roof drains shall be designed in accordance with CPC 1106.4.

- CHAPTER 24 GLASS AND GLAZING

- U.	GLASS AND GLAZING

- Each pane of safety glazing installed in hazardous locations shall be identified by a manufacturer’s designation specifying who applied the designation, the manufacturer or installer and the safety glazing standard. The following shall be considered specific hazardous locations for the purposed of safety glazing. Glazing in: (CBC 2406)

- a.	Swinging doors.

- b.	Fixed and sliding panels of sliding door assemblies and panels in sliding and bi-fold closet door assemblies.

- c.	Storm doors.

- d.	Unframed swinging doors.

- e.	Doors and enclosures for hot tubs, whirlpools, saunas, steam rooms, bathtubs, and showers.

- f.	Fixed or operable panels adjacent to a door where the nearest exposed edge of the glazing is within 24” arc of either vertical edge of the door in a closed position and where the bottom exposed edge of the glazing is less than 60” above the walking surface.

- g.	Fixed or operable panel, other than described in items e and f, which meets all of the following conditions (read code for exception with special installation).

- i.	Exposed area of an individual pane greater than 9 sq. ft.

- ii.	Exposed bottom edge less than 18” above the floor.

- iii.	Exposed top edge greater than 36” above the floor.

- iv.	One or more walking surfaces within 36” horizontally of the plane of the glazing.

  - Guards and railings regardless of area or height above a walking surface. Included are structural baluster panels and nonstructural in-fill panels.

- i.	Walls and fences enclosing indoor and outdoor swimming pools and spas where all of the following conditions are present:

- i.	The bottom edge of the glazing is less than 60” above a walking surface on the pool or spa side of the glazing.

- ii.	The glazing is within 60” of a swimming pool or spa water’s edge.

  - Adjacent to stairways, landings and ramps within 36” horizontally of a walking surface; when the exposed surface of the glass is less than 60” above the plane of the adjacent walking surface (read code for exception with special installation).

- k.	Adjacent to stairways within 60” horizontally of the bottom tread of a stairway in any direction when the exposed surface of the glass is less than 36” above the nose of the tread (read code for exception with special installation).

- For glass handrails and guards, the panels and their support system shall be designed to withstand the loads specified in Chapter 16. A safety factor of four shall be used. The min. nominal thickness of the glass shall be 1/4”. Specify approved report number and manufacturer of glass panel guardrail on plans and/or detail. (CBC 2407)

- Skylights set at an angle of less than 45 degrees from the horizontal plane shall be mounted at least 4” above the plane of the roof on a curb constructed as required for the frame. Except for R-3 occupancies, skylights without a curb shall be permitted on roofs with a min. slope of 14 degrees (3 units vertical in 12 units horizontal) per CBC 2405.4 and 2610.2. Glass skylights shall comply with CBC 2405. Plastic skylights shall comply with CBC 2610.

- CHAPTER 25 GYPSUM BOARD AND PLASTER

- V.	GYPSUM BOARD AND PLASTER

- A corrosion resistant weep screed, min. 26 galv. sheet gage, is required below the stucco at the foundation plate line a min. 4" above earth or 2" above paved area with a vertical attachment flange of 3.5”. Weep screeds shall be of a type which will allow trapped water to drain to the exterior of the building. Show these dimensions on a foundation detail drawing. (CBC 2512.1.2)

- Cement, fiber-cement or glass mat gypsum backers in compliance with ASTM C1178, C1288 or C1325 shall be used as a base for wall tile in tub and shower areas and wall and ceiling panels in shower areas. Water-resistance gypsum backing board shall be used as a base for tile in water closet compartment walls when installed in accordance with GA-216 or ASTM C840. Regular gypsum wallboard is permitted under tile or wall panels in other wall and ceiling areas when installed in accordance with GA-216 or ASTM C840. Water-resistant gypsum board shall not be used in the following locations: (CBC 2509.2)

  - Over a vapor retarder.

  - In areas subject to continuous high humidity, such as saunas, steam rooms or gang shower rooms.

  - On ceilings where frame spacing exceeds 12” o.c. for 1/2” thick water-resistant gypsum backing board and more than 16” o.c. for 5/8” thick water-resistant gypsum backing board.

- In areas subject to continuous high humidity, such as saunas, steam rooms or gang shower rooms.

- W.	ADDITIONAL WRITTEN COMMENTS

| No. | ###### Comment | Code Sec. No. |
| --- | --- | --- |