## Sheet1
| Guide sheet Name | Guide sheet Items | Pass/No Pass/NA
M10 | M10 UNDERGROUND | Approved Plans on site (CMC 114.2) | INFORMATION ONLY
|  | For Restaurants / Food Service facilities have Health Dept. approved and stamped plans on site | INFORMATION ONLY
M11 | M11 RADIANT / COILS | Hydronic heating systems shall be installed in accordance with the manufacturers approved installation instructions (AMI) and verified with those documents available on site | INFORMATION ONLY
The equipment, material, and labor necessary for testing shall be furnished by the person or permit holder that is requesting the inspection (CMC 1201.2.8.1)
The piping shall be tested with water (CMC 1201.2.8.2)
Piping shall be tested with a hydrostatic pressure of at least 50 psig greater than the operating pressure but not less than 100 psig (CMC 1201.2.8.3)
Required tests shall be conducted in the presence of the inspector and piping shall remain exposed to the inspector. Test pressure shall be maintained for at least 30 minutes without indications of a leak (CMC 1201.2.8.3)
All piping, tubing, and fitting materials shall be free of defects and comply with nationally recognized standards approved by the AHJ (CMC 1201.3.1.6
M20 | M20 UNDERFLOOR DUCTS | Duct work shall not be restricted. (Minimum bending radius of 1X duct diameter) AMI & CMC | INFORMATION ONLY
Suspended equipment min 6in above grade (CMC 904.3.1.2)
Passageway min 22in wide×30in high (CMC 904.11.1)
Passageway max distance 20ft to equipment EXC (CMC 904.11.2)
| DUCTS | Factory-made ducts listed and labeled & installed AMI (CMC 602.3)
Ground clearance min 4in (CMC 604.2 & 3)
18in vertical clearance where needed under duct to prevent cutting off access to crawl space (CMC 604.1A)
Duct joints sealed, taped, or gasketed airtight (CMC 602.4)
Flex duct per listed and labeled (1-1/2in strap every 4ft) (CMC T6-10)
Flex ducts req UL-181B pressure-sensitive tape (CMC 602.4)
| DUCT SUPPORT | Support of ducts to be per manufacturers listed instructions AMI or absent documentation:
• Flex duct - 1-1/2" strap every 4ft with sag a maximum of 1/2" per foot
• Round metal duct - min 1/2" metal straps or 12 gauge wire every 10ft
| Insulation in Unconditioned space (1in fiberglass ≈ R-3) | R-6 min in floor trusses, R-8 elsewhere EXC (CMC 605.0)
M21 | M21 RADIANT / COILS | Hydronic heating systems shall be installed in accordance with the manufacturers approved installation instructions (AMI) and verified with those documents available on site | INFORMATION ONLY
The equipment, material, and labor necessary for testing shall be furnished by the person or permit holder that is requesting the inspection (CMC 1201.2.8.1)
The piping shall be tested with water (CMC 1201.2.8.2)
Piping shall be tested with a hydrostatic pressure of at least 50 psig greater than the operating pressure but not less than 100 psig (CMC 1201.2.8.3)
Required tests shall be conducted in the presence of the inspector and piping shall remain exposed to the inspector. Test pressure shall be maintained for at least 30 minutes without indications of a leak (CMC 1201.2.8.3)
All piping, tubing, and fitting materials shall be free of defects and comply with nationally recognized standards approved by the AHJ (CMC 1201.3.1.6
M30 | M30 SUSPENDED CEILING/VAVs/COILS | Equipment must be listed and labeled (CMC 303.1)
Verify that UL-181 listed tape is used at all duct connection. (UL 181 B FX is for flexible ducts, UL 181 A is for rigid ducts)
| DUCTS | Factory-made ducts listed and labeled & installed AMI (CMC 602.3)
Metal ducts per SMACNA standards or CMC T-6 -1&8 (CMC 602.5)
Duct joints sealed, taped, or gasketed airtight (CMC 602.4)
Metal duct supports max 10ft intervals or per IBC (CMC T6-7)
| FACTORY MADE DUCTS | Flex duct per listed and labeled (1-1/2in strap every 4ft) (CMC T6-10)
Flex ducts req UL-181B pressure-sensitive tape (CMC 602.4)
|  | Terminal devices shall be supported independently of the flexible duct. | AMI
Factory-made duct supports AMI and/or as set forth in the ANSI.SMACNA 006-2006 Standard (CMC 604.5)
Flex ducts supports shall be spaced per manufactured specification, but no more than 4’ and max. Sag 2” or ½” max. per foot. UMC standard 6-5 sec. A.6.509, Residential Energy Manual
|  | Duct work shall not be restricted. (Minimum bending radius of 1X duct diameter) Sharper bends increase pressure drop significantly and reduce airflow. | AMI
Factory-made duct Shall not be used for vertical risers serving more than two stories in height. (CMC 604.3)
|  | Use the minimum length of flexible duct to make connections. Excess length of flexible duct shall not be installed to allow for possible future relocations of air terminal devices | AMI
| PLENUMS | No combustibles in plenums used for return air. Plastic plumbing pipe, insulation with exposed facing, nonfire-resistent treated wood, etc. (CMC 602.2)
| MECHANICAL SERVICES | Must be positively attached to the suspension system main beams or to cross tees with the same load carrying capacity. | INFORMATION ONLY
|  | Maintain required working clearances as required by mechanical, electric, and plumbing codes. | INFORMATION ONLY
|  | Air diffusers and other ceiling-mounted services weighing less than 20 lb must have positive attachment to the ceiling grid. In addition to positive attachment to the grid, services weighing between 20 lb and 56 lb must have two 12 gauge safety wires connected to the structure above or to the ceiling hanger wires to prevent them from falling. Two diagonally opposite vertical safety wires can keep them from posing a risk to occupants below. Services weighing above 56 lb must be supported directly from the structure above by approved hangers; in some cases this can be accomplished with 4 taut 12 gauge wires, one located at each corner of the service. While ASTM E580/E580M-10a does not require safety wires for items weighing less than 20 lb, use of at least one wire may be good practice considering the number of diffusers that have come down in recent earthquakes. | INFORMATION ONLY
|  | Terminals or services weighing more than 56 lbs must be independently supported. | INFORMATION ONLY
| CONDENSATE DISPOSAL | Condensate drains from air-cooling coils and similar equipment shall be collected and discharged to an approved plumbing fixture or disposal area (CPC 814.1)
Condensate drains shall be of approved corrosion resistant materials not smaller the outlet size and sized as indicated in CMC Table 8-2. Drain shall have a slope of not less than 1/8" per foot or 1 percent (CPC 814.1)
Condensate drains shall drain by gravity and discharge into an indirect connection to the drainage system through an airgap or airbreak (CPC 814.3)
Equipment in above ceiling space and/or furred space provided with condensate drains shall be provided with secondary drains and/or pans that drain to a visible location that can be readily observed (CMC 309.2)
|  | Condensate pumps allowed if required due to elevation with approval of AHJ and with stipulations. Pumped discharge only to nearest connection to a min. 3/4" drain sloped as required to point of disposal. (LOCAL) | INFORMATION ONLY
M31 | M31 DAMPER (FIRE,CEILING,SMOKE) | All documentation of manufacturers installation instructions including supplemental must be maintained and made available for review by the AHJ (Authority Having Jurisdiction). | INFORMATION ONLY
• Fire Dampers
|  | Fire dampers shall be installed per manufacture's instructions and NFPA 90A. | INFORMATION ONLY
• Smoke Dampers
|  | Only dampers designed and tested per UL 555 and UL 555S shall be installed. | INFORMATION ONLY
|  | Installation. Fire dampers, smoke dampers, combination fire/smoke dampers and ceiling radiation dampers located within air distribution and smoke control systems shall be installed in accordance with the requirements of this section, and the manufacturer's installation instructions and listing. | INFORMATION ONLY
| FIRE RESISTANCE RATINGS | • Fire dampers used for the protection of openings in walls, partitions, or floors with fire resistance ratings of less than 3 hours shall have a 11⁄2 hour fire protection rating in accordance with UL555, NFPA90A (Chapter 3-4.1 & 3-4.2) | INFORMATION ONLY
| FIRE RESISTANCE RATINGS | • Fire Dampers used for the protection of openings in walls, partitions, or floors having a fire resistance rating of 3 hours or more shall have a 3 hour fire protection rating in accordance with UL555, NFPA90A (Chapter 3-4.1 & 3-4.2) | INFORMATION ONLY
| FIRE AND COMBINATION FIRE/SMOKE DAMPER INSTALLATION REQUIREMENTS | Combination fire/smoke dampers have the following installation requirements:
• Expansion gap
|  | Typically the fire wall opening must be a minimum of 1⁄4" larger than the width and height of the damper/sleeve assembly. The expansion gap must increase 1⁄8" for each foot the damper exceeds 2' on the width or height. Consult the manufacturers installation instructions | AMI
• Sleeve requirements
|  | The specific sleeve requirements depend on the damper size and type of duct to sleeve connection. As a general rule, the sleeve thickness must be equal to or thicker than the duct connected to it. Consult the manufacturers installation instructions for more details on UL sleeve length limitations. | AMI
• Mounting Orientation
|  | Fire dampers are required to pass a test for vertical mount and/or a test for horizontal mount. Dampers need to be installed in the correct orientation to ensure life safety and proper fire protection. Each vertical or horizontal mount damper carries its own label. These mounting orientations are no longer interchangeable. Consult the manufacturers installation instructions | AMI
• Installing damper /sleeve assembly in wall and floor openings -
|  | Installation options for securing the damper to wall or floor openings depend on the following factors: model, size, mounting orientation, and wall or floor construction. Single side or two side retaining angle options are available. Check with local authority having jurisdiction. See installation instructions for detail. | AMI
• Retaining Angles
|  | • Minimum 1-1/2" X 1-1/2" X 16 ga | AMI
|  | • 16 gage is most commonly used thickness for retaining angles. Consult the manufacturers installation instructions for specifics. | AMI
|  | • Retaining angles must overlap structure opening 1 inch minimum and cover corners of openings | AMI
|  | • Retaining angle attachment to sleeve and to structure to be manufacturers installation instructions. Standard installations call for single angle installation to be attached to sleeve and structure and double angles to be attached only to sleeve. For attachment spacing consult manufacturers installation instructions for specifics. | AMI
• Damper to sleeve connections
|  | The manufacturer’s installation instructions are required to show the method of attaching the damper to the sleeve and the spacing of the attachments. | AMI
• Sealing of the damper frame to the ductwork
|  | On smoke and combination fire smoke dampers, the joint between the damper frame and duct must be sealed to prevent unwanted air leakage. | AMI
• Duct-to-sleeve connections
|  | These can be rigid or breakaway type. Breakaway connections should be described in detail in the manufacturer’s installation instructions. | AMI
|  | • Damper size and RIGID or BREAKAWAY duct-to-sleeve connections determine the required sleeve thickness. There are no requirements for sleeves heavier than 14 ga. (1.9 mm) and with BREAKAWAY connections, the sleeve can be the same gauge as the connecting ductwork. | AMI
|  | Combination fire smoke dampers must be qualified under UL Standard 555 as a fire damper AND under UL Standard 555S as a smoke damper. The considerations listed above for both of these damper types apply to the selection and application of combination fire smoke dampers. | INFORMATION ONLY
|  | Access points shall be permanently identified on the exterior by a label having letters not less than 1/2 inch (12.7mm) in height reading: FIRE/SMOKE DAMPER, SMOKE DAMPER, or FIRE DAMPER | INFORMATION ONLY
M32 | M32 MU AIR / OUTDOOR AIR | Natural or mechanical ventilation req’d for all occupied spaces (CMC 402.1) | INFORMATION ONLY
| NATURAL VENTILATION | Naturally ventilated spaces must be permanently open to and within 25 ft of operable wall or roof openings to the outdoors, the openable area of which is a minimum of 4% of the net occupiable floor area being naturally ventilated. (The net occupiable floor area is measured from the inside surfaces of the walls, excluding permanently enclosed obstructions such as shafts and columns.) (CMC 402.2) | INFORMATION ONLY
| MECHANICAL VENTILATION | Mechanical Ventilation - Mechanical outdoor ventilation must be provided for all spaces normally occupied that are not naturally ventilated. The Standards require that a space conditioning system provide outdoor air equal to or exceeding the ventilation rates required for each of the spaces that it serves. (CMC 402.3) | INFORMATION ONLY
|  | Filters. In mechanically ventilated buildings, provide regularly occupied areas of the building with air filtration media for outside & return air prior to occupancy that provides at least a MERV of 8 | INFORMATION ONLY
|  | Mechanical and gravity outdoor air intake openings shall be located a minimum of 10 feet from any hazardous or noxious contaminant, such as vents, chimneys, plumbing vents, streets, alleys, parking lots and loading docks, except as otherwise specified in this code. Where a source of contaminant is located within 10 feet of an intake opening, such opening shall be located a minimum of 2 feet below the contaminant source. For the purpose of this section, the exhaust from dwelling unit toilet rooms, bathrooms and kitchens shall not be considered as hazardous or noxious. | ASHRAE STANDARDS
| Insulation in Unconditioned space (1in fiberglass ≈ R-3) | Portions of the supply and return ducts located in any of the following places shall be insulated to a minimum level of R-8:
o Outdoors;
o In a space between the roof and an insulated ceiling;
o In a space directly under a roof with fixed vents or opening to the outside or unconditioned spaces;
o In an unconditioned crawlspace;
o In other unconditioned spaces
Portions of the supply duct that are not located in any of the listed spaces (unconditioned space), including ducts buried in concrete slabs, shall be insulated to a minimum installed level of R-4.2 (or any higher level required by CMC section 605) or be enclosed in conditioned space. (CMC 605.0)
Manufactured ducts must be supported & stretched so they are as straight as possible without kinks that obstruct airflow.
Insulation may be omitted on that portion of a duct which is located within a wall or a floor to ceiling space where:
o Both sides of the space are exposed to conditioned air.
o The space is not ventilated.
o The space is not used as a return plenum.
o The space is not exposed to unconditioned air.
Ceilings which form plenums need not be insulated.
NOTE: Where ducts are used for both heating and cooling, the minimum insulation shall be as required for the most restrictive condition.
R-6 min in floor trusses, R-8 elsewhere EXC (CMC 605.0)
| Pollutant Control (CGC 5.504) | Covering of duct openings & protection of mechanical equipment during construction. At the time of rough installation or during storage on the construction site & until final startup of the heating & cooling equipment, all duct & other related air distribution component openings shall be covered with tape, plastic, sheet metal or other methods acceptable to the enforcing agency to reduce the amount of dust or debris which may collect in the system per CGC 5.504.3 | INFORMATION ONLY
| MAKE UP AIR | In commercial cooking areas replacement air shall be provided that is adequate to prevent negative pressure in the cooking area from exceeding 0.02 inch water column. When fire extinguishing system discharges, makeup air supplied internally to a hood shall be shut off (CMC 511.3 & NFPA 96:8.3.1 - 8.3.2)
Makeup air req’d approximately = to exhaust air (CMC 511.3)
Interlock w/ exhaust to ensure adequate makeup air (CMC 511.3)
|  | Note: Part of the necessary makeup air—typically 20%—can be provided by transfer from other spaces inside the building as long as negative pressures are avoided in the kitchen | INFORMATION ONLY
Intake min 10ft from vents & exhaust outlets (CMC 506.9.2)
M33 | M33 DUCT (TYPE l HOOD) | Listed grease ducts shall be installed per their listings and manufacturers instructions. (CMC 510.4)
Required to be constructed of and supported by carbon steel not less than 0.054 inch (#16 MSG) thickness or stainless steel not less than 0.043 inch ( No. 18 MSG) in thickness. (CMC 510.5)
|  | Connections and welds shall be substantially connected and smooth. | INFORMATION ONLY
Horizontal duct shall have a slope of not less than 1/4 inch per lineal foot toward the hood or toward an approved grease reservoir. When horizontal ducts exceed 75 feet in length, the slope shall not be less than 1 inch per lineal foot. (CMC 507.2.3)
|  | All seams, joints, and penetrations of the hood enclosure shall have liquid tight continuous external welds to the hoods lower outermost perimeter. Internal joints are required to be made grease tight. | INFORMATION ONLY
Welds to duct systems to be liquid tight and continuous and be made with overlapping duct connections of either telescoping or bell type joints, no butt-weld connections allowed. The inside duct section shall always be uphill of the outside duct section. (CMC 510.5.2.2)
|  | Duct welds to be inspected prior to concealment and/or fire wrap installation | INFORMATION ONLY
| CLEARANCE REQUIREMENTS | Where enclosures are not required, hoods, duct, grease removal devices and fans shall have clearance per CMC Section 507.2: (CMC 507.2 & NFPA 96:4.2.1)
o Eighteen (18) inches to combustible materials
o Three (3) inches to limited-combustible materials
o Zero (0) inches to noncombustible materials
Where enclosures are required, hoods, duct, grease removal devices and fans shall have clearance per CMC Section 510.7.2: (CMC 507.2 & NFPA 96)
o Eighteen (18) inches to enclosures of combustible materials
o Six (6) inches to enclosures of noncombustible or limited combustible materials
o Provisions for reducing clearances as described in CMC Section 507.2 are not applicable to enclosures
|  | Ducts shall not come in contact with combustible surfaces. | INFORMATION ONLY
| Field applied and factory built grease duct enclosures | Fire barrier duct wrap shall be maintained when duct passes through wall and installed by a certified installer. CMC 507.2.3
|  | Duct wrap 3-M or equivalent | INFORMATION ONLY
|  | Shall be a UL 2221 Listed assembly and installed per the manufacturers installation. | INFORMATION ONLY
|  | Ensure no physical damage may occur to any material or product. | INFORMATION ONLY
|  | Verify number of wraps and attachment methods. Inspection is required | INFORMATION ONLY
|  | Provide manufacturers installation instructions upon request for listed duct wrap | INFORMATION ONLY
| ACCESS/CLEANOUTS | Change of duct direction requires accessible cleanout. (CMC 510.3.1)
Horizontal ducts shall have at least one 20” x20” opening for personnel entry and shall be secured sufficiently to allow for the weight of personnel entry to duct. When openings of this size are not possible, openings large enough to permit cleaning shall be provided at 12’ foot intervals. Supports 24” and larger shall be designed for the weight of the ductwork plus 800 lbs at any point of the duct system. (CMC 510.3.4.1)
Vertical ductwork where personnel entry is possible, access shall be provider at the top of the vertical riser to accommodate descent. Were personnel entry is not possible, adequate access for cleaning shall be provided on each floor. (CMC 510.3.4.1)
Exhaust fans with ductwork connected to both sides shall have access for cleaning and inspection within 3’ feet of each side of fan. (CMC 510.3.3)
Access panels shall be listed grease duct access door assemblies, or shall be constructed of materials described in CMC 510.3.4.4 (CMC 510.3.4)
Signage shall be placed on all access panels stating the following:
o ACCESS PANEL-DO NOT OBSTRUCT. (CMC 510.1.6)
M34 | M34 DETECTORS (DUCT, CO) | Air- moving systems supplying air in excess of 2000 cubic feet per minute to enclosed spaces within buildings shall be equipped with an automatic shutoff. Shutoff to be accomplished by interrupting the power source of the air moving equipment upon detection of smoke in the main supply air duct served by such equipment. Duct detectors to be installed as required. (CMC 609.0)
Exceptions to duct detector requirements are listed in CMC 609.0 EXC 1,2,3,4,5 (CMC 609.0)
Duct detectors must be listed and labeled and installed in accordance with AMI. (CMC 609.0)
| CO DETECTORS | Detectors must be installed in all dwelling units that contain a fossil fuel burning heater, appliance, or fireplace; or that have an attached garage. (A fossil fuel is coal, kerosene, oil, wood, fuel gases, and other petroleum or hydrocarbon products that emit carbon monoxide as a byproduct of combustion). Heres the installation schedule: | CA HEALTH AND SAFETY CODE §§ 3260 & §§ 17926
§§ July 1, 2011: all single-family homes
§§ January 1, 2013: all other dwelling units (such as multi-family residences
|  | ASHRAE Standard. ANSI/ASHRAE Standard 62-1989 (ASHRAE 1989) requires the ventilation of spaces even when they are not continuously occupied (such as parking garages) | ANSI/ASHRAE Standard
NFPA states that all enclosed, basement, and underground parking structures shall be ventilated by a mechanical system capable of providing a minimum of six air changes per hour during hours of normal operation. CMC requires 14,000 cfm of exhaust air for each operating vehicle, based on 2.5 percent of all parking spaces, and not less than one (1). (CMC 403.8.2.1)
National Fire Protection Association. NFPA defines enclosed parking structures as buildings or structures that are used for the parking of motor vehicles, which have enclosure walls that represent less than 25% of the total wall area open to the atmosphere at each level using at least two sides of the structure (NFPA 1994).
Enclosed Parking Garages. Mechanical ventilation systems for enclosed parking garages are not required to operate continuously where the system is arranged to operate automatically upon detection of a concentration of carbon monoxide of 25 parts per million by approved automatic detection devices.” (CMC 403.8.2)
Automatic CO sensing device may be employed tp modulate the ventilation system to maintain a maximum average concentration of CO of 50 ppm during any eight-hour (8) period. A maximum concentration not greater than 200 ppm for a period not exceeding one (1) hour shall also be required. CO sensing devices shall be approved and listed. Install according to CMC, NFPA, and AMI. (CMC 403.8.2.2)
|  | Contaminant sensors can be used to control the amount of ventilation supplied to the garages. The acceptable contaminant levels are based on U.S. Environmental Protection Agency recommendations. In particular, the ASHRAE standard limits the CO exposure level to 35 ppm for one 21 hour and to 9 ppm for eight hours. For NO2 exposure, the ASHRAE limit is 0.25 ppm for one hour. | INFORMATION ONLY
|  | In addition to the indoor air quality procedure, Standard 62 specifies a ventilation rate for enclosed parking garages of 1.5 cubic feet per minute per square foot of floor area (1.5 cfm/ft2) | INFORMATION ONLY
M35 | M35 EXHAUST DUCTS | Minimum ventilation rates for occupancies are to be established from CMC and ASHRAE requirements for all areas normally occupied. Provide adequate ventilation per CMC Table 4-1 and Table 4-7 (CMC & ASHRAE 62.1 Table 6-1)
Environmental exhaust ducts shall terminate outside the building and be equipped with a back-draft damper (CMC 504.3.1)
Exhaust ducts under positive pressure shall not extend into or pass through ducts or plenums (CMC 602.1)
Exhaust outlets shall be 3 feet from the property line and 3 feet from any opening into the building (CMC 504.5)
Exhaust outlets for product conveying systems shall be 10 feet from the property line, 3 feet from exterior roof/wall, 10 feet from any openings into the building and 10 feet above grade (CMC 510.8.2.1 & 510.8.3.1)
| LAUNDRY EXHAUST | Commercial laundry equipment to be exhausted with material size and type and as listed with the manufacturers approved listings. All installation materials to be on site and presented at time of inspections. (CMC 504.3.3)
Show make up air for laundry exhaust systems (CMC 504.3.2 & 905.3 (B))
Exhaust for domestic dryers shall be 4 inches minimum and shall not exceed a total length of 14 feet including two (2) 90 degree elbows. Two (2) feet shall be deducted for each 90 degree elbow in excess of two (2) (CMC 504.3.2.2)
| TOILET ROOMS EXHAUST | Toilet rooms in commercial buildings to have required cfm/air changes per CMC Table 4-4 (CMC T4-4)
Toilets rooms in residential buildings to have required cfm/air changes per CMC Table 4-1 & 4-4 (CMC T4-1)
| GENERAL REQUIREMENTS | Duct type and size as required by equipment manufacturers listed installation instructions and/or CMC
Factory-made ducts listed and labeled & installed AMI (CMC 602.3)
Metal ducts per SMACNA standards or CMC T-6 -1&8 (CMC 602.5)
Duct joints sealed, taped, or gasketed airtight (CMC 602.4)
Metal duct supports max 10ft intervals or per IBC (CMC T6-7)
Flex duct per listed and labeled (1-1/2in strap every 4ft) (CMC T6-10)
M38 | M38 FRAME O.K. | OK to cover pending Bldg/Elec/Plbg | INFORMATION ONLY
M40 | M40 REGISTERS/GRILLS | All Registers, Diffusers, Grills, Filters, etc. installed and complete | INFORMATION ONLY
Outside air openings req screens w/ mesh >=1/4in (CMC 701.9 B)
No screens allowed on ducts terminating in attic (CMC 701.10 (5))
Net free area of louvers 75% for metal, 25% for wood (CMC 701.9 A)
Motorized louvers/dampers req appliance interlock (CMC 701.9 C)
No manual dampers in C.A. ducts (CMC 701.9 C)
Exterior openings min 12in above finished ground (CMC 701.10 (6))
Laundry exhaust end outside in backdraft damper & no screens (CMC 504.3)
Environmental ducts require backdraft damper & outdoor termination required EXC (CMC 504.1)
|  | Mechanical and gravity outdoor air intake openings shall be located a minimum of 10 feet from any hazardous or noxious contaminant, such as vents, chimneys, plumbing vents, streets, alleys, parking lots and loading docks, except as otherwise specified in this code. Where a source of contaminant is located within 10 feet of an intake opening, such opening shall be located a minimum of 2 feet below the contaminant source. For the purpose of this section, the exhaust from dwelling unit toilet rooms, bathrooms and kitchens shall not be considered as hazardous or noxious. | ANSI/ASHRAE Standard
|  | Exhaust air shall not be directed onto walkways | ANSI/ASHRAE Standard
|  | Air exhaust and intake openings that terminate outdoors shall be protected with corrosion-resistant screens, louvers or grilles having a minimum opening size of 1/4 inch and a maximum opening size of 1/2 inch, in any dimension. Openings shall be protected against local weather conditions. Outdoor air exhaust and intake openings shall meet the provisions for exterior wall opening protectives in accordance with this code. | ANSI/ASHRAE Standard
M41 | M41 EQUIPMENT | Approved Plans on site (CMC 114.2) | INFORMATION ONLY
|  | For Restaurants / Food Service facilities have Health Dept. approved and stamped plans on site | INFORMATION ONLY
|  | All equipment and appliances to be installed are required to be approved by the AHJ, be listed and labeled, and to conform to the requirements as indicated in CMC Chapter 3, Sections 301 through 303, as well as all other pertinent sections of Chapter 3, NFPA requirements, Health Department, and Fire. | INFORMATION ONLY
|  | All manufacturers installation instructions as well as all required supplemental documentation to remain on site and available at time of inspections. | INFORMATION ONLY
| COMMERCIAL / INDUSTRIAL HOODS | Environmental hoods to be type, size, and installed as required by CMC Chapter 5 Section 504.0 | INFORMATION ONLY
|  | Design and installation of product-conveying ventilation systems shall conform to the requirements of AMI, CMC Chapter 5, Sections 505 through 506, and NFPA | INFORMATION ONLY
|  | Design and installation of Commercial hoods and kitchen ventilation systems shall conform to the requirements of AMI, CMC Chapter 5, Sections 507 through 517, and NFPA | INFORMATION ONLY
|  | Where required, any clearance reduction method used for equipment, ducting, etc. shall comply with AMI, CMC Chapter 5 Table 5-2 & Table 5-3 and NFPA | INFORMATION ONLY
|  | For Restaurants / Food Service facilities verify that equipment / appliances such as hoods, fans, grease removal devices, etc. are as indicated on approved and stamped plan set. All revisions to approved plans to be submitted for approvals by Health prior to sign-off. | INFORMATION ONLY
| EQUIPMENT/APPLIANCES | Equipment/appliance clearances from combustible materials and/or for service access shall be per listed manufactures installation, NFPA, or CMC Chapter 3, Table 3-2. (CMC 303.3)
When more than one heating, cooling, ventilating, or other types of equipment is installed on the roof or in a building, it shall be permanently identified as to the area or space served by the equipment. (CMC 303.6)
Equipment and/or appliances that are designed to be fixed in position shall be securely fastened in place and seismic braced as required. Supports for equipment shall be designed and constructed to sustain vertical and horizontal loads within the stress limitations specified in the Building Code. (CMC 303.4)
Appliances with casters shall be limited in movement by restraining devices installed in accordance with the connector and appliance manufacturers installation instructions. (CMC 303.5)
All equipment requiring an external source of electrical power for its operation shall be provided with: (CMC 303.8.1.6)
• Readily accessible disconnect within sight of the equipment
• A grounding type receptacle on the roof and/or adjacent to the equipment.
M42 | M42 ROOF ACCESS/GUARDS | Equipment and appliances in all areas shall be accessible for inspection, service, repair, and replacement. Sufficient clearances shall be maintained as per manufacturer, NFPA, and/or the CMC. Unless otherwise specified not less than thirty (30) inches in depth, width, and height or space shall be provided. (CMC 304.0 & 304.1)
At least six (6) feet between any part of the equipment and the edge of a roof or similar hazard must be maintained or installation of a rigidly fixed rail, guard, parapet, or other building structure at least forty-two (42) inches in height shall be provided on the exposed side. (CMC 303.8.1.5 & 304.1.2.2)
Buildings more than fifteen (15) feet in height shall have an inside means of access to the roof, unless other means acceptable to the AHJ are used. (CMC 304.1.2)
M43 | M43 ENERGY CODE | Verification and/or documentation of installations compliance with the California Energy Code and Cal Green to be completed and submitted to the building department prior to final occupancy | INFORMATION ONLY
| ENERGY CODE | Provide original copies of correctly filled out Certificates of Acceptance forms for the field inspector at or prior to the final inspection. | INFORMATION ONLY
|  | Required Energy Efficiency Standards Compliance Forms (2008 EES): | INFORMATION ONLY
|  | • MECH-1C through -4C as applicable, will need to be completed and submitted with the permit application. | INFORMATION ONLY
|  | • Installation certificates for Mechanical MECH-2A through MECH-15A, MECH-4 HERS (if applicable), forms will need to be completed by both the installing contractor and HERS rater as applicable. Copies shall be made available for the inspector at Final Inspection for the energy features that require acceptance testing. | INFORMATION ONLY
Requests for information and forms should be directed to the California Energy Commission at:
California Energy Commission
1516 Ninth Street
Sacramento, CA 95814
916-654-5106 or
www.energy.ca.gov/title24
M44 | M44 CAL GREEN | Testing and adjusting. Testing and adjusting of systems shall be required for buildings less than 10,000 square feet per CGC 5.410.4. | CAL GREEN
|  | Operation and maintenance manual. Provide the building owner with detailed operating and maintenance instructions and copies of guaranties/warranties for each system prior to final inspection per CBC 5.410.4.5. | CAL GREEN
|  | Inspections and reports. Include a copy of all inspection verifications and reports required by the enforcing agency. | INFORMATION ONLY
| GAS FIREPLACES | Install only a direct-vent sealed-combustion gas or sealed wood-burning fireplace or a sealed woodstove and refer to residential requirements in the California Energy Code, Title 24, Part 6, Subchapter 7, Section 150. | CAL GREEN
|  | Woodstoves. Woodstoves shall comply with US EPA Phase II emission limits. | CAL GREEN/EPA
| POLUTION CONTROL | POLUTANT CONTROL (CGC 5.504)
|  | Covering of duct openings and protection of mechanical equipment during construction. At the time of rough installation or during storage on the construction site and until final startup of the heating and cooling equipment, all duct and other related air distribution component openings shall be covered with tape, plastic, sheet metal or other methods acceptable to the enforcing agency to reduce the amount of dust or debris which may collect in the system per CGC 5.504.3. | CAL GREEN
|  | Hazardous particulates and chemical pollutants. Minimize and control pollutant entry into buildings and cross contamination of regularly occupied areas. | CAL GREEN
|  | Filters. In mechanically ventilated buildings, provide regularly occupied areas of the building with air filtration media for outside and return air prior to occupancy that provides at least a MERV of 8. | CAL GREEN
M45 | M45 SI REPORTS (EQ, BALANCE) | Provide copies and/or report verification for third party Mechanical ventilation systems air balance reports as well as any reports for testing equipment, duct leak testing, start-up of equipment, etc. as may be required. | INFORMATION ONLY
|  | Provide original copies of correctly filled out Certificates of Acceptance forms for the field inspector at or prior to the final inspection. Include installation certificates for Mechanical MECH-2A through MECH-15A, MECH-4 HERS (if applicable) as required. | INFORMATION ONLY
M86 | M86 FINAL MECHANICAL | Final occupancy OK'd pending Bldg, Elec, Plbg.