## Sheet1
| Guide sheet Name | Guide sheet Items | Pass/No Pass/NA
P10 | P10 UNDERGROUND | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
| DWV | For Restaurants / Food Service facilities have Health Dept. approved and stamped plans on site | INFORMATION ONLY
Verify restroom facilities conform to CPC Chapter 4 requirements for minimum sanitary facilities and that they conform to the requirements for handicap accessibility standards (CPC Table 4-1)
|  | Plastic DWV piping not allowed per Oakland Amendments to the 2010 CPC and/or Oakland Municipal Code | INFORMATION ONLY
Cast Iron with NSF and CI logo (Chapter 14 and City standards)
2 band NH Couplings w/shear rings and NSF logo CITY STANDARD
|  | No piping shall be directly embedded in concrete (CPC313.0) | INFORMATION ONLY
|  | Pipe supported on firm bed entire length (CPC 301.0) | INFORMATION ONLY
No rocks supporting or touching pipe until 12" above pipe (CPC 315.4)
1/4" per ft grade required-1/8th" per ft must first be approved by the AHJ (CPC 708.0)
Cleanouts may be omitted on branches less than 5' except for sinks and urinal and fixtures above the first level of plumbing Cleanouts are required for changes of direction exceeding 135 degrees (CPC 707.0)
Cleanouts shall be installed on the connection of the Building Sewer and Building Drain within 2 ft of the Building exterior for the installation of Overflow prevention device (CPC 719.1 and City OMC)
Cleanouts must have 12" front clearance for 2" pipe and less and 18" for over 2" pipe (CPC 707.9)
All DWV pipe and fittings shall be in a drainage pattern until 6'' above the fixture flood rim of the fixtures served (CPC 905.3)
| SUDS RELIEF | Provide provision for suds relief ( 8ft seperation of connections ) for all verticle to horizontal changes of direction off stacks carrying 3-stories or more of suds-producing fixtures. (CPC 711.0)
• Bathtubs
• Laundries
• Washing Machines
• Kitchen Sinks
• Dishwashers
| VERTICLE WET VENTING | Min 2" (CPC 908.2.3)
Wet-vented fixtures must be on same floor level (CPC 908.1&2)
Vertical wet venting max 4 fixtures, max 6ft, limited to 1- & 2-WSFU fixtures & wet vent min 1 pipe size larger than required waste (CPC 908.1)
|  | Verify requirement for backwater valve protection or direct contractor to establish elevations of finished floor and upstream manhole rim. (CPC 710.1) | INFORMATION ONLY
Vertical to horizontal or horizontal to horizontal through wye branches or 45° wye branches or equivalent (drainage pattern) (CPC 706.3 & 4)
No flat venting (takeoff above horizontal centerline) (CPC 905.3)
Sanitary tee OK only for horizontal to vertical (CPC 706.2)
| TESTING | Test all piping before cover or concealment (CPC 1.8.4.4 & 103.5.1)
DWV water test min. 10ft head for 15 minutes OR + Air test 5psig (10in mercury) for 15 minutes . Air not approved for plastic piping (CPC 712.2)
Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (609.4)
|  | Piping shall be inspected prior to backfilling trench | INFORMATION ONLY
|  | Contact Health department for inspection prior to cover rough in-ground DWV | INFORMATION ONLY
| WATER | All underground water piping within the building shall be minimum Type L copper and any and all joints shall be brazed (CPC 604.2 & 609.3)
Any other underground water piping proposed for within the Building must first be approved by the AHJ
Type L copper tubing shall be installed without joints if possible. Where joints are permitted, they shall be brazed and fittings shall be wrought copper. Type M copper is prohibited. (CPC 609.3.2)
Water service material may be any material referenced in (CPC table 6-4) and installed according to its listing
| GAS | No gas piping is allowed underground with the building unless proven to be unavoidable to the AHJ (1211.1.6)
Any approved underground gas piping inside the building shall be sleeved and vented to the exterior of the building. The sleeve must be sealed in the building and must be a material that can withstand the super imposed loads and gas pressure. The vent shall be installed to prevent water and insect intrusion (CPC 1211.1.6)
Approved non metallic piping shall be installed outside underground only by a (CPC 1211.1.7)
P11 | P11 BACKWATER VALVE | Backwater valve required for fixtures w/ FLR below upstream manhole cover {CPC: on floor level below cover} (CPC 710.1)
Backwater valve must remain accessible for service (CPC 710.6)
Fixtures {on floor level} above manhole cover may not drain through backwater valve (CPC 710.1)
Cleanouts labeled for drains through backwater valve (CPC 710.1)
P12 | P12 INTERCEPTOR (SO) | Sand and/or Sand/Oil interceptors are required when-ever the AHJ deems it advisable to protect the drainage system from harmful discharges (CPC 1016.1)
|  | Sand/Oil interceptor is required for restaurant trash enclosures equipped with wash down fixtures | LOCAL
|  | Exterior trash enclosures to be protected from rain water (Covered) and sloped or bermed so as not to receive surface water from the exterior. | LOCAL
|  | Sand/Oil interceptor discharge to be routed to the sanitary sewer | INFORMATION ONLY
|  | Sand/oil interceptor to be installed per manufacturers installation instructions and 2010 CPC, interceptor to be primed, vented, and floor to sloped to drain. | INFORMATION ONLY
|  | Sand/oil interceptors will be required at all restaurants with warewashing sinks, enclosed parking garages, every public or private wash rack or floor area used for cleaning machinery or machine parts, or other facilities deemed by the AHJ as requiring drainage protection | LOCAL
P13 | P13 INTERCEPTOR (GREASE) | Where it is determined by the Authority Having Jurisdiction (AHJ) that waste pretreatment is required, an approved type of grease interceptor/s complying with the provisions of the 2010 CPC and EBMUD requirements shall be installed. Interceptors are to be correctly sized and properly installed per 2010 CPC and Approved Manufacturers Installation instructions (AMI). | INFORMATION ONLY
Water closets, urinals, and other plumbing fixtures conveying human waste shall not drain into or through the grease interceptor (CPC 1014.1)
Pot sinks and dishwashing sinks shall be directly connected to the drainage system (CPC 704.3)
Pot Sinks – A floor drain shall be provided adjacent to the fixture and the fixture shall be connected on the sewer side of the floor drain trap provided that no other drainage line is connected between the floor drain waste connection and the fixture drain (CPC 704.3)
| HGI | Plumbing fixtures connected to a Type A and B Hydromechanical Grease Interceptor | INFORMATION ONLY
A = external flow control with air intake vent, directly connected.
B = external flow control without air intake vent, directly connected)
shall discharge through an approved type of vented flow control installed in a readily accessible and visible location. Vented flow control shall be located such that no system vent shall be between the flow control and the grease interceptor inlet (CPC 1014.2.1)
A vent shall be installed downstream of HGI's in accordance with the requirements of the CPC and AMI (CPC 1014.2.3)
| GRAVITY INTERCEPTOR | Gravity interceptors shall be constructed in accordance with the applicable standard in 2010 CPC Table 14-1 or the design approved by the AHJ (CPC 1014.3.3)
Gravity interceptors shall not be installed in any part of a building where food is handled. Location of the grease interceptor shall meet the approval of the AHJ (CPC 1014.3.4)
The sizing criteria for a gravity interceptor shall be determined by using 2010 CPC Table 10-3, manufacturer's specifications, and as specified in ASME A112.14.6 as listed in the 2010 CPC Table 14-1 (CPC 1014.3.6 & CPC 1015.4)
Floor drain shall be installed in commercial kitchens (CPC 412.2.2)
Pot Sinks – A floor drain shall be provided adjacent to the fixture and the fixture shall be connected on the sewer side of the floor drain trap provided that no other drainage line is connected between the floor drain waste connection and the fixture drain (CPC 704.3)
Each fixture discharging into a HGI shall be individually trapped and vented (CPC 1014.1.1)
P20 | P20 UNDERFLOOR | Approved Plans on site (CPC 103.3.2)
| DWV | Health Dept. approved and stamped plans on site | INFORMATION ONLY
|  | Verify restroom facilities conform to CPC Chapter 4 requirements for minimum sanitary facilities and that they conform to the requirements for handicap accessibility standards (CPC Table 4-1) | INFORMATION ONLY
|  | Plastic DWV piping not allowed per Oakland Amendments to the 2010 CPC and/or Oakland Municipal Code | INFORMATION ONLY
|  | Cast Iron with NSF and CI logo (Chapter 14 and City standards) | INFORMATION ONLY
|  | 2 band NH Couplings w/shear rings and NSF logo CITY STANDARD | INFORMATION ONLY
1/4" per ft grade required-1/8th" per ft must first be approved by the AHJ (CPC 708.0)
Cleanouts may be omitted on branches less than 5' except for sinks and urinal and fixtures above the first level of plumbing Cleanouts are required for changes of direction exceeding 135 degrees (CPC 707.0)
Cleanouts shall be installed on the connection of the Building Sewer and Building Drain within 2 ft of the Building exterior for the installation of Overflow prevention device (CPC 719.1 and City OMC)
Cleanouts must have 12" front clearance for 2" pipe and less and 18" for over 2" pipe (CPC 707.9)
All DWV pipe and fittings shall be in a drainage pattern until 6'' above the fixture flood rim of the fixtures served (CPC 905.3)
|  | Contact Health department for inspection prior to cover rough in under floor | INFORMATION ONLY
|  | Verify requirement for backwater valve protection or direct contractor to establish elevations of finished floor and upstream manhole rim. | INFORMATION ONLY
| SUDS RELIEF | Provide provision for suds relief ( 8ft seperation of connections ) for all verticle to horizontal changes of direction off stacks carrying 3-stories or more of suds-producing fixtures. (CPC 711.0)
• Bathtubs
• Laundries
• Washing Machines
• Kitchen Sinks
• Dishwashers
| WATER SYSTEM | Min water service 3/4in (CPC 610.8)
Size according to H20 fixture units, pressure and elevation (CPC 610.0)
No reduction to inlet of service by softener, backflow (CPC 610.2)
Support per tables and/or manufacturers installation requirements. (CPC 314.1)
Excessive pressure >80psi must be regulated (CPC 608.2)
|  | Use of plastic domestic water piping has additional installation requirements as noted in the Plumbing code. Maintain manufacturers installation quides on site and install per manufacturers and 2010 CPC requirements. | INFORMATION ONLY
Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (CPC 609.4)
Isolate copper lines from contact with dissimilar metals (CPC 316.2.4)
Burred ends of pipe and tubing shall be reamed to the full bore of the pipe or tube (CPC 310.3)
Hangers and support spacing as per Table 3-2 CPC (CPC 314.0)
Allow for thermal expansion & contraction ( IS 5&9)
| GAS SYSTEM | Size pipe per tables, provide sizing layout and calcs as required (CPC 1217.1)
No unions or bushings in concealed locations, Unions only allowed at appliance connections with valve (CPC 1211.3.2 and Oakland Amendments)
P21 | P21 DRAINS - FIRE TEST/CONDENSATE/MISC | Condensate may not drain to public way or over public way (CPC 309.1)
May drain to indirect receptor (lav tailpiece, Service/Mop sink) (CPC 309.1)
Protect from condensate overflow w/ one of following: + Secondary drain line higher than primary drain Protect from condensate overflow w/ one of following:+ Drain pan w/ interlocked detector (CPC 309.2)
Secondary discharge to readily observable location (CPC 309.2)
| FIRE SPRINKLER INSP TEST DRAIN | When fire sprinkler systems are installed and/or altered the inspectors inspection test drain will be required to be routed to an approved landscape area if allowed by the determination of the Fire Department or routed to an indirect sanitary stand-pipe drain. The hub drain provided to be a minimum of three (3) inch with an increase in size of the hub to no less than four (4) inch. As required by the California Clean Water Act | LOCAL
|  | Fire test hub drain to be connected to the sanitary sewer, trapped, vented, and primed with a minimum of a one (1) inch air gap maintained | LOCAL
P22 | P22 FLOOR RECEPTORS | Provide approved drains as may be required for water heater T&P line, Condensate drainage for A/C, Refrigeration units, Condensing appliances, etc. | INFORMATION ONLY
Food preparation sinks, steam kettles, dipper wells, and other equipment having drainage connections and used for the storage of items used for human ingestion or used in direct contact with ready to eat food shall discharge through an air gap or air break into a trapped and vented receptor (CPC 801.2.3)
Indirect waste piping shall discharge into the building drainage system through an air gap or air break as set forth by the 2010 CPC (CPC 801.1)
The minimum vertical distance as measured from the lowest point of the indirect waste pipe or fixture outlet to the flood level rim of the receptor shall be not less than one (1) inch (CPC 801.1)
| FLOOR DRAINS | 412.2.2 Floor drain shall be installed in commercial kitchens.
Pot Sinks – A floor drain shall be provided adjacent to the fixture and the fixture shall be connected on the sewer side of the floor drain trap provided that no other drainage line is connected between the floor drain waste connection and the fixture drain (CPC 704.3)
Floor drains shall be installed in the following areas:
* Toilet rooms containing two (2) or more water closets or a combination of one (1) water closet and one (1) urinal (CPC 411.2.1)
* Commercial kitchens and in accordance with 2010 CPC Section 704.3 (CPC 411.2.2)
* Laundry rooms in commercial buildings and common laundry facilities in multi-family dwelling buildings (CPC 411.2.3)
| FLOOR DRAINS AND RECEPTOR TRAPS | Floor drain and/or receptor traps shall be located so that they can be readily cleaned and in full view, Floor sinks located with access, ex. Half in half out from under equipment (CPC 1006.0)
Floor drains or similar traps connected to the drainage system and subject to infrequent use shall be protected with a trap seal primer, trap seal primer to be valved and accessible for maintenance (CPC 1007.0)
|  | Floor drains shall be level with finish floor in commercial kitchens or other facilities subject to Health Dept. inspections otherwise floor sinks to be set at one (1) inch above the finished floor | LOCAL
| TESTING | Test all piping before cover or concealment (CPC 1.8.4.4 & 103.5.1)
DWV water test min. 10ft head for 15 minutes OR + Air test 5psig (10in mercury) for 15 minutes . Air not approved for plastic piping (CPC 712.2)
Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (609.4)
Gas test min 10 psi for 15 minutes (Oakland Amendments)
P30 | P30 DWV PIPING | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
|  | Plastic DWV piping not allowed per Oakland Amendments to the 2010 CPC and/or Oakland Municipal Code | INFORMATION ONLY
All DWV pipe and fittings shall be in a drainage pattern until 6'' above the fixture flood rim of the fixtures served (CPC 905.3)
Hangers not to abrade pipe (no metal straps in contact) (IS 5&9)
Support to resist sagging & distortion or upward thrust (CPC 314.2)
Hangers and support spacing as per Table 3-2 CPC (CPC 314.0)
Allow for thermal expansion & contraction ( IS 5&9)
Rain water shall not connect to sanitary system (CPC 714.2)
Size according to DFU load (CPC 703.1)
Vertical to horizontal or horizontal to horizontal through wye branches or 45° wye branches or equivalent (CPC 706.3 & 4)
Sanitary tee OK only for horizontal to vertical (CPC 706.2)
Double sanitary tee OK if barrel of fitting is 2 pipe sizes larger than inlets (CPC 706.2)
Fire blocking around ceiling/floor plate penetrations (CPC 1501.0)
Steel plate if <1-1/2in {1in UPC} from framing edge (CPC 313.9)
Tailpiece max vertical distance 24in except clothes washer 30in (CPC 1001.4)
| VENTS | Where vents connect to a horizontal drainage pipe, each vent pipe shall have it's invert taken off above the drainage centerline of the horizontal pipe (CPC 905.2)
Vents below fixture FLR must be drainage pattern (CPC 905.3)
No flat venting (takeoff above horizontal centerline) (CPC 905.3)
Vent opening above weir (toilet excepted) (CPC 905.5)
{Aggregate vent area must be >= building sewer in CPC} {904.1}
Horizontal vent min 6in above fixture flood rim of fixture (CPC 905.3)
| NOTCHING / BORING | Steel-plate protection for pipes other than galvanized & cast iron in notches or holes < 1½ in. (1 in. UPC) of face of framing (CPC 313.9)
Protection min 2 in. above sole plates & below top plates
Protection min 1½ in. beyond outside of pipe (CPC 313.9*)
Protective plates min 18 gage (CPC 313.9)
Drilling & notching per T34, (CPC 313.2)
Notching 25% max in bearing wall, 40% nonbearing (CPC 602.6)
Bored holes min 5/8 in. from face of stud (CPC 602.6)
Boring 40% max in bearing wall, 60% nonbearing EXC F71, (CPC 602.6)
• 2 successive doubled bearing studs 60% OK F71 (CPC 602.6)
If top plate > 50% removed for pipes, attach galvanized 16-gage metal tie 1½ in. wide with min 8-10d nails each side of notch EXC (CPC 602.6.1)
P31 | P31 GAS PIPING | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
Rough piping inspection - shall be made after the gas piping authorized by the permit has been installed and before any such piping has been covered or concealed. This inspection shall include a determination that the gas sizing, material, and installation meet the requirements of the 2010 CPC (CPC 1204.3.1)
Size pipe per tables, provide sizing layout and calcs as required (CPC 1209.5.3.2)
Main shutoff required outdoors at each building (CPC 1211.11.3)
Material: steel (galv or black), type K or L Cu, CSST (CPC 1209.5.3.2)
Interior of pipe or tubing must be deburred (CPC 1209.5.5)
Support per tables and CPC 1211.2.6 (CPC 314.1 & 1211.2.6)
No unions or bushings in concealed locations, Unions only allowed at appliance connections with valve (CPC 1211.3.2 and Oakland Amendments)
|  | CSST Gas piping requires certified installer, provide pocket certifications as required by manufacturer | INFORMATION ONLY
P32 | P32 WATER PIPING | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
Min water service 3/4in (CPC 610.8)
Size according to H20 fixture units, pressure and elevation (CPC 610.0)
No reduction to inlet of service by softener, backflow (CPC 610.2)
Support per tables and/or manufacturers installation requirements. (CPC 314.1)
Excessive pressure >80psi must be regulated (CPC 608.2)
All building water supply systems in which quick-acting valves are installed shall be provided with mechanical pressure-absorbing devices that are listed and approved. Water hammer arrestors are to be installed as close as possible to the quick-acting valves (CPC 609.10)
|  | Use of plastic domestic water piping has additional installation requirements as noted in the Plumbing code. Maintain manufacturers installation quides on site and install per manufacturers and 2010 CPC requirements. | INFORMATION ONLY
Isolate copper lines from contact with dissimilar metals (CPC 316.2.4)
Burred ends of pipe and tubing shall be reamed to the full bore of the pipe or tube (CPC 310.3)
| TESTING | Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (CPC 609.4)
P33 | P33 SHOWER PAN | Approved Plans on site (CPC 103.3.2)
Shower walls nonabsorbent to min 72 in. above drain (CPC IS-4.6}
|  | Diameter is measured to center of threshold. | INFORMATION ONLY
Min area 1024 sq. in. & min diameter 30 in. measured from finished wall (CPC 411.7)
Curb min 2in & max 9in (CPC 411.6)
Finished threshold height min 1 in. below rest of shower receptor & 2–9 in. above top of drain (CPC 411.6)
Door min 22 in. wide (CPC 411.6)
Door must open outward (CPC 411.6)
Secure shower valve, head/riser to permanent structure (CPC 411.11)
Listed anti-scald/pressure balance valve req’d 120˚F max (CPC 418.0)
Slope underlayment ¼ in./ft. (CPC 411.8)
Liner min 3 in. above dam (CPC 411.8)
Pan liner plastic or 3 layers hot mop type 15 felt (CPC 411.8)
Weep holes at drain req’d & must remain clear (CPC 411.8)
No fasteners < 1 in. above finished threshold (CPC 411.8)
Roll over top of rough threshold (no penetrations through top) & fasten to outside edge (CPC 411.8)
|  | Outside dimensions: IAPMO listed—39½ in. Min rough pan {34in×34in CPC} | INFORMATION ONLY
P34 | P34 BACKFLOW DEVICES | Cross connection control shall be provided in accordance with the provisions of the 2010 CPC, AHJ, and EBMUD requirements (CPC 603.0)
Backflow devices shall be listed and approved and shall be tested at the time of installation. Test results to be submitted to EBMUD and/or the AHJ prior to final occupancy (CPC 603.1)
Potable water supply to carbonators shall be protected by either an air gap or a vented backflow preventer, material and type as required and listed and approved for that use (CPC 603.4.12)
Atmospheric vacuum breakers OK for: Hose connections (not needed for tank drain valves) (CPC 603.4.7)
Irrigation system, 6 in. above highest head F63 (CPC T6-2)
Integral air gaps in fixtures to recognized standards OK for: Pullout spouts & sprayers with integral backflow AMI (CPC 603.3.7). Pull-out or separate shower spray wands (CPC 603.3.7)
P38 | P38 FRAME O.K. | OK to cover pending Bldg/Elec/Mech
P40 | P40 WATER SERVICE | Min water service 3/4in (CPC 610.8)
|  | Water service material may be any material referenced in CPC table 6-4 and installed according to its listing | INFORMATION ONLY
Any non-metallic water service shall be accompanied by a 18 awg blue tracer wire exposed at both ends (CPC 604.8 exc)
|  | size according to H20 fixture units, pressure and elevation | INFORMATION ONLY
No reduction to inlet of service by softener, backflow (CPC 610.2)
Accessible full-bore main shutoff required (CPC 605.2)
Excessive pressure >80psi must be regulated (CPC 608.2)
Expansion tank required for regulators w/o integral bypass & for building supplies w/ check valves (CPC 608.2&3)
Backflow protection from fire sprinkler piping w/ fire department connection or w/ additives or antifreeze (CPC 603.4.16)
P41 | P41 GAS TEST | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
|  | Final piping inspection - This inspection shall be made after the piping authorized by the permit has been installed and after all portions that are to be covered are covered or concealed. This test shall be in accordance with 2010 CPC Section 1214.1 and test gauges shall comply with Section 319.0 and/or Oakland Amendments to the 2010 CPC (CPC 1204.3.2) | LOCAL
| TEST GUAGES | Test gauges shall not have a pressure range exceeding twice the test pressure applied (CPC 319.4)
Required pressure tests exceeding ten (10) psi but less than or equal to one-hundred (100) psi shall be performed with gauges of one (1) psi increments or less (CPC 309.2)
|  | The test pressure shall be not less than 1.5 times the proposed maximum working pressure, but not less than 10 psi gauge pressure. For welded fuel piping and for fuel piping with proposed maximum working pressure exceeding 14 inches of water column, the test pressure shall be not less than 60 psi gauge pressure. Oakland Amendments to the 2010 CPC (OMC 15.04.950) | LOCAL
|  | All necessary apparatus for conducting pressure tests shall be furnished in good working order by the permit holder. Gauges shall comply with section 319.0. All pressure tests shall be witnessed during the inspection, and there shall be no perceptible reduction in pressure throughout the time period of the test. Oakland Amendments to the 2010 CPC (OMC 15.04.945) | LOCAL
P42 | P42 UTILITY RELEASE | Gas meter release only submitted to PG&E after completion of the final gas pressure test, inspection of all equipment that utilizes gas for installation to code, all seismic bracing requirements, and proper installation of all safety devices for equipment. After approval for Plumbing and Mechanical aspects of the gas equipment final approval to be subject to the building inspector | LOCAL
P43A | P43A ENERGY CODE / CAL GREEN | Water Efficiency & Conservation - Indoor Water Use (CGC 5.303) | CAL GREEN
|  | Meters. Separate meters shall be installed for the uses described in Sections 503.1.1 through 503.1.2. | CAL GREEN
|  | Buildings in excess of 50,000 square feet. Separate submeters shall be installed as follows: | CAL GREEN
|  | 1. For each individual leased, rented or other tenant space within the building projected to consume more than 100 gal/day. | CAL GREEN
|  | 2. For spaces used for laundry or cleaners, restaurant or food service, medical or dental office, laboratory or beauty salon or barber shop projected to consume more than 100 gal/day. | CAL GREEN
|  | Excess consumption. Any building within a project or space within a building that is projected to consume more than 1,000 gal/day | CAL GREEN
|  | 20 percent savings. A schedule of plumbing fixtures & fixture fittings that will reduce the overall use of potable water within the building by 20 percent shall be provided per CGC 5.303.2. (Calculate savings by Water Use Worksheets) | CAL GREEN
|  | Multiple showerheads serving one shower. When single shower fixtures are served by more than one showerhead, the combined flow rate of all the showerheads shall not exceed the maximum flow rates specified in the 20 percent reduction column contained in Table 5.303.2.3 or the shower shall be designed to only allow one showerhead to be in operation at a time (CGC 5.303.2.1). | CAL GREEN
| CAL GREEN | Wastewater reduction. Each building shall reduce the generation of wastewater by one of the methods per CGC 5.303.4: | CAL GREEN
|  | Plumbing fixtures & fittings. Plumbing fixtures (water closets & urinals) & fittings (faucets & showerheads) shall comply with the requirements listed for each type in Items listed in Table 5.303.6: | CAL GREEN
1. Water closets (toilets) – flushometer valve type single or dual flush, maximum flush volume
2. Water closets (toilets) – tank type
3. Urinals, maximum flush volume
4. Urinals, non-water urinals
5. Public lavatory faucets : Maximum flow rate-0.5 gpm
6. Public metering self-closing faucets : Maximum flow rate-0.25 gallon per cycle
7. Residential bathroom lavatory sink faucets: Maximum flow rate-1.5 gpm
| Outdoor Water Use | Water budget. A water budget shall be developed for landscape irrigation use per CGC 5.304.1 | CAL GREEN
|  | Outdoor potable water use. For new water service, separate meters or submeters shall be installed for indoor & outdoor potable water use for landscaped areas between 1,000 square feet & 5,000 square feet per CGC 5.304 | CAL GREEN
P44 | P44 CHLORINATION / SI REPORTS | New or repaired potable water systems shall be disinfected prior to use as required by the AHJ. Disinfection of the water system to be done by an approved third party agency, as prescribed by the 2010 CPC Sections 609.1 through 609.4, and/or as directed by the AHJ. (CPC 609.9 & Local) | INFORMATION ONLY
Disinfection and/or test results by an approved third party agency to be submitted to the building inspector prior to the final occupancy of the building (Local)
P86 | P86 FINAL PLUMBING | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
|  | For Restaurants / Food Service facilities have Health Dept. approved and stamped plans on site | INFORMATION ONLY
Verify restroom facilities conform to CPC Chapter 4 requirements for minimum sanitary facilities and that they conform to the requirements for handicap accessibility standards (CPC Table 4-1)
Verify that all plumbing installations for persons with disabilities comply with the California Code of Regulations, Title 24, Part 2, Chapter 11A and/or Chapter 11B as applicable (CPC 407.6)
|  | Plastic DWV piping not allowed per Oakland Amendments to the 2010 CPC and/or Oakland Municipal Code | INFORMATION ONLY
|  | All plumbing fixtures and/or appliances to be installed, connected and ready for testing and inspection prior to scheduled final inspection | INFORMATION ONLY
| APPLIANCE SHUT-OFFS / CONNECTIONS | Shutoff valve ahead of union & <=6ft of appliance EXC (CPC 1212.5)
Max length connector 6ft (CPC 1212.5)
Flex connectors completely in same room as appliance (CPC 1212.1)
Connector not through appliance housing EXC
Sediment trap close as practical to appliance EXC (CPC 1212.7)
Gas-fired food service (commercial cooking) equipment listed for use with casters or otherwise moveable shall be connected in accordance with the appliance connector manufacturers installation instructions and shall be installed with approved seismic restraint devices installed as directed (CPC 1212.1)
|  | Fire blocking and caulking as required shall be completed at All-Trades inspection prior to insulation NO EXCEPTIONS. | INFORMATION ONLY
|  | Fire rated walls: All plastic pipe such as condensate lines, vacuum lines, exhaust lines, drain lines, waste & vent lines require an approved U.L. tested fire stop collar or equivalent at fire rated wall/ceiling OR use cast iron for DWV pipes. Fire stop all penetrations to fire rated walls and/or floors | INFORMATION ONLY
Food or drink shall not be stored, prepared, or displayed beneath soil or drain pipe, unless those areas are protected against leakage or condensation from such pipes reaching the food or drink. (CPC 318) When necessary provide protection using the following methods:
* Provide proper seepage pan.
* Seal watertight all openings.
* Thermally insulate condensation pipes.
| WATER HEATERS | Full-open valve required on cold water supply (CPC 605.2)
Unions required within 12in for service and removal (CPC 609.5)
|  | Electric WH requires in-sight or lockable disconnect {see Electrical Appliances: Required Disconnecting Means} | INFORMATION ONLY
Fuel-fired WH prohibited in storage closets (local)
Fuel-fired WH prohibited in bedroom, bathroom, or their closets EXC (CPC 505.1)
Ignition source >=18in above garage floor EXC (CPC 508.14)
Protection from vehicles required in garage (CPC 508.14)
Seismic restraint upper & lower 1/3rd of tank in SDC D & townhouses in SDC C {all occupancies in SDC C, D, E & F in CPC (CPC 508.2)
Min 30in working space in front (UMC)
Min closet door size 24in wide
Attic: solid passage floor max 20ft, min 24in wide (CPC 509.4)
Air for combustion, ventilation, and dilution of flue gases for gas appliances shall be obtained by the application of one of the methods covered in the 2010 CPC Sections 507.2.1 through 507.7, methods covered in the 2010 CPC Section 507.4 through 507.7, and/or the manufacturers installation instructions (AMI) (CPC 507.1)
Attic equipment requires light and receptacle near WH (CPC 509.4.5)
Watertight corrosion resistant pan req'd for water heaters located where leakage could cause damage (CPC 508.4)
Metallic Piping to be Bonded continuously with copper bonding wire and bonding clamps to cold, hot, and gas lines to tie systems together at water heater, using a #8 for 100 amp service and a #6 for 200 amp service. (C.E.C. 2010 250.104)
Venting System shall be constructed, sized appropriately, and installed to code per manufacturer’s installation instructions; in no case shall vent piping be smaller than required for water heater’s draft diverter or venting outlet. (CPC 510.10.3)
Water Piping Insulation shall be installed 5 feet on the cold and 5 feet on the hot water supplies at water heater when possible and maintain 6” clearance from vent and flue. NOTE: If water heater has a recirculating pump system, the entire length of circulating piping loop will need to be insulated (2010 California Energy Commission Mandatory Requirements/Title 24)
Thermal-Expansion Tank System shall be required to protect water heater and water piping system from excess pressure due to thermal-expansion and set per manufacturer’s installation instructions. (CPC 608.3 & CMC 1006.0)
| TPR SAFETY VALVE | Combination TPRV required in CPC (CPC 608.3)
Size at least same as outlet & serve only one valve (CPC 608.5)
t&P cannot terminate in overflow pan (CPC 508.5)
6–24in CPC from ground, floor, or receptor (CPC 608.5)
Individual shutoff (may be at manifold) required for each fixture or appliance (CPC 605.5)
Fixtures smooth, impervious & free from concealed fouling areas (CPC 401.1)
Joint between fixtures & walls or floors sealed (CPC 407.2)
Air gap device above FLR required for Dishwasher drain (CPC 807.4)
Water closet seats - All water closet seats except those within dwelling units, shall be either of the open front types or have an automatic seat cover dispenser, seats for public buildings shall conform to the standard listed in the 2010 CPC Table 14-1 (CPC 408.2)
| Fixtures for persons with disabilities | Fixtures for use by persons with disabilities shall conform to the appropriate standards as referenced in the California Code of Regulations, Title 24, Part 2, Chapter 11A and/or Chapter 11B as applicable (CPC 413.0)
| PUBLIC LAVATORIES | Hot water delivered from public-use lavatories shall be limited to a maximum temperature of 1200 by a device that conforms to ASSE 1070 or CSA B125.3. The water heater thermostat shall not be considered a control for meeting this provision. (CPC 413.1)
| DOCUMENTATION | Provide copy of sterilization/test report to building inspector prior to occupancy (LOCAL) | INFORMATION ONLY
|  | If new testable backflow devices have been install on the domestic water supply - provide the building inspector a copy of test report by an approved 3rd party tester as well as the required copy to EBMUD (LOCAL) | INFORMATION ONLY
|  | Provide original copies of correctly filled out Certificates of Acceptance forms for the field inspector at or prior to the final inspection. | INFORMATION ONLY
|  | Required Energy Efficiency Standards Compliance Forms (2008 EES): | INFORMATION ONLY
|  | • MECH-1C through -4C as applicable, will need to be completed and submitted with the permit application. | INFORMATION ONLY
|  | • Installation certificates for Mechanical MECH-2A through MECH-15A, MECH-4 HERS (if applicable), forms will need to be completed by both the installing contractor and HERS rater as applicable. Copies shall be made available for the inspector at Final Inspection for the energy features that require acceptance testing. | INFORMATION ONLY
Requests for information and forms should be directed to the California Energy Commission at:
California Energy Commission
1516 Ninth Street
Sacramento, CA 95814
916-654-5106 or
www.energy.ca.gov/title24