## Sheet1
| Guide sheet Name | Guide sheet Items | Pass/No Pass/NA
RP10 | RP10 UNDERGROUND | Approved Plans on site (CPC 103.3.2)
| DWV | If plastic DWV used - determine number of floor levels indicated on plans and on site for compliance with Oakland amendments to the 2010 CPC | INFORMATION ONLY
Cast Iron with NSF and CI logo (Chapter 14 and City standards)
|  | 2 band NH Couplings w/shear rings and NSF logo CITY STANDARD | INFORMATION ONLY
No piping shall be directly embedded in concrete (CPC313.0)
Provide for movement (expansion & contraction) (CPC 313.2)
|  | Pipe supported on firm bed entire length (CPC 301.0) | INFORMATION ONLY
No rocks supporting or touching pipe until 12" above pipe (CPC 315.4)
1/4" per ft grade required-1/8th" per ft must first be approved by the AHJ (CPC 708.0)
Cleanouts may be omitted on branches less than 5' except for sinks and urinal and fixtures above the first level of plumbing Cleanouts are required for changes of direction exceeding 135 degrees (CPC 707.0)
|  | Piping shall be inspected prior to backfilling trench (CPC 1.8.4.4 & 103.5.1) | INFORMATION ONLY
Cleanouts shall be installed on the connection of the Building Sewer and Building Drain within 2 ft of the Building exterior for the installation of Overflow prevention device (CPC 719.1 and City OMC)
Cleanouts must have 12" front clearance for 2" pipe and less and 18" for over 2" pipe (CPC 707.9)
|  | Is a curbless shower being installed-submit plan for AHJ APPROVAL BEFORE POUR | INFORMATION ONLY
All DWV pipe and fittings shall be in a drainage pattern until 6'' above the fixture flood rim of the fixtures served (CPC 905.3)
Piping passing through foundation walls shall be sleeved and sealed watertight (CPC 313.0)
| WATER | All underground water piping within the building shall be minimum Type L copper and any and all joints shall be brazed (CPC 604.2 & 609.3)
|  | Any other underground water piping proposed for within the Building must first be approved by the AHJ | INFORMATION ONLY
Type L copper tubing shall be installed without joints if possible. Where joints are permitted, they shall be brazed and fittings shall be wrought copper. Type M copper is prohibited. (CPC 609.3.2)
Water service material may be any material referenced in (CPC table 6-4) and installed according to its listing (CPC table 6-4)
Any non-metallic water service shall be accompanied by a 18 awg blue tracer wire exposed at both ends (CPC 604.8 exc)
| GAS | No gas piping is allowed underground with the building unless proven to be unavoidable to the AHJ (1211.1.6)
Approved non metallic piping shall be installed outside underground only by a (CPC 1211.1.7)
|  | Plastic gas piping installation requires the installer to be certified | INFORMATION ONLY
RP11 | RP11 BACKWATER VALVE / EJECTORS | Is backwater valve required -first floor of plumbing below upstream manhole cover -only floor levels with fixtures below the upstream manhole cover shall discharge through the backwater valve (CPC 710.0)
Ejector system Approved by AHJ and installed-dual pumps 20 gpm min-2 FU per gallon (CPC 710.0)
| TESTING | Test all piping before cover or concealment (CPC 1.8.4.4 & 103.5.1)
DWV water test min. 10ft head for 15 minutes OR + Air test 5psig (10in mercury) for 15 minutes . Air not approved for plastic piping (CPC 712.2)
Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (609.4)
Gas test min 10 psi for 15 minutes (Oakland Amendments)
RP20 | RP20 UNDERFLOOR | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
| DWV | If plastic DWV used - determine number of floor levels indicated on plans and on site for compliance with Oakland amendments to the 2010 CPC | INFORMATION ONLY
| UNDERFLOOR ACCESS | 18in min clearance EXC (CPC 707.9)
Location must remain accessible (CPC 707.9)
Cast Iron with NSF and CI logo (Chapter 14 and City standards)
|  | 2 band NH Couplings w/shear rings and NSF logo CITY STANDARD | INFORMATION ONLY
1/4" per ft grade required-1/8th" per ft must first be approved by the AHJ (CPC 708.0)
Cleanouts may be omitted on branches less than 5' except for sinks and urinal and fixtures above the first level of plumbing Cleanouts are required for changes of direction exceeding 135 degrees (CPC 707.0)
Cleanouts shall be installed on the connection of the Building Sewer and Building Drain within 2 ft of the Building exterior for the installation of Overflow prevention device (CPC 719.1 and City OMC)
Cleanouts must have 12" front clearance for 2" pipe and less and 18" for over 2" pipe (CPC 707.9)
|  | Is a curbless shower being installed-submit plan for AHJ APPROVAL BEFORE POUR | INFORMATION ONLY
All DWV pipe and fittings shall be in a drainage pattern until 6'' above the fixture flood rim of the fixtures served (CPC 905.3)
Hangers not to abrade pipe (no metal straps in contact) (IS 5&9)
Support to resist sagging & distortion or upward thrust (CPC 314.2)
Hangers and support spacing as per Table 3-2 CPC (CPC 314.0)
Allow for thermal expansion & contraction ( IS 5&9)
Rain water shall not connect to sanitary system (CPC 714.2)
Size according to DFU load (CPC 703.1)
Min drain slope 1/4 in/ft [1/8 in/ft OK for 4" with prior approval only] (CPC 708.0)
Vertical to horizontal or horizontal to horizontal through wye branches or 45° wye branches or equivalent (CPC 706.3 & 4)
Sanitary tee OK only for horizontal to vertical (CPC 706.2)
Double sanitary tee OK if barrel of fitting is 2 pipe sizes larger than inlets (CPC 706.2)
No flat venting (takeoff above horizontal centerline) (CPC 905.3)
Horizontal vent min 6in above fixture flood rim of fixture (CPC 905.3)
Vent opening above weir (toilet excepted) (CPC 905.5)
Fire blocking around ceiling/floor plate penetrations (CPC 1501.0)
Steel plate if <1-1/2in {1in UPC} from framing edge (CPC 313.9)
Tailpiece max vertical distance 24in except clothes washer 30in (CPC 1001.4)
Horizontal vent min 6in above fixture flood rim of fixture (CPC 905.3)
Aggregate vent area must be >= building sewer in CPC (CPC 904.1)
| Island Sinks: UPC Drain Loop Method | Vents below fixture FLR must be drainage pattern (CPC 905.3)
Island sink vented w/ drain-type fittings only (CPC 909.0)
Vent must be on down steam side of loop (CPC 909.0)
No upstream fixtures allowed on island drain (CPC 909.0)
Island sink cleanout in vertical section of foot vent, accessible and above floor regardless of location in building (story) (CPC 909.0)
Limited to sinks & lavs only (1 and 2 fixture unit fixtures) (CPC 909.0)
| VERTICLE WET VENTS | Min 2" (CPC 908.2.3)
Wet-vented fixtures must be on same floor level (CPC 908.1&2)
Vertical wet venting max 4 fixtures, max 6ft, limited to 1- & 2-WSFU fixtures & wet vent min 1 pipe size larger than required waste (CPC 908.1)
Test all piping before cover or concealment (103.5.1)
DWV water test min. 10ft head for 15 minutes OR + Air test 5psig (10in mercury) for 15 minutes . Air not approved for plastic piping (CPC 712.2)
| WATER | Min water service 3/4in (CPC 610.8)
Size according to H20 fixture units, pressure and elevation (CPC 610.0)
No reduction to inlet of service by softener, backflow (CPC 610.2)
Support per tables and/or manufacturers installation requirements. (CPC 314.1)
Excessive pressure >80psi must be regulated (CPC 608.2)
|  | Use of plastic domestic water piping has additional installation requirements as noted in the Plumbing code. Maintain manufacturers installation quides on site and install per manufacturers and 2010 CPC requirements. | INFORMATION ONLY
Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (609.4)
Isolate copper lines from contact with dissimilar metals (CPC 316.2.4)
Burred ends of pipe and tubing shall be reamed to the full bore of the pipe or tube (CPC 310.3)
| WATER | Water service material may be any material referenced in CPC table 6-4 and installed according to its listing
Any non-metallic water service shall be accompanied by a 18 awg blue tracer wire exposed at both ends (CPC 604.8 exc)
| GAS | No gas piping is allowed underground with the building unless proven to be unavoidable to the AHJ (CPC 1211.1.6)
Any approved underground gas piping inside the building shall be sleeved and vented to the exterior of the building. The sleeve must be sealed in the building and must be a material that can withstand the super imposed loads and gas pressure. The vent shall be installed to prevent water and insect intrusion (CPC 1211.1.6)
Approved non metallic piping shall be installed outside underground only by a (CPC 1211.1.7)
Locate gas meter in accessible & ventilated space (CPC 1209.6.2A)
Size pipe per tables, provide sizing layout and calcs as required (CPC 1217.1)
No unions or bushings in concealed locations, Unions only allowed at appliance connections with valve (CPC 1211.3.2 and Oakland Amendments)
| BACKWATER VALVES & EJECTORS | Is backwater valve required -first floor of plumbing below upstream manhole cover -only floor levels with fixtures below the upstream manhole cover shall discharge through the backwater valve (CPC 710.0)
Ejector system Approved by AHJ and installed-dual pumps 20 gpm min-2 FU per gallon (CPC 710.0)
RP30 | RP30 DWV | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
|  | If plastic DWV used - determine number of floor levels indicated on plans and on site for compliance with Oakland amendments to the 2010 CPC | INFORMATION ONLY
|  | Is a curbless shower being installed-submit plan for AHJ APPROVAL BEFORE POUR | INFORMATION ONLY
All DWV pipe and fittings shall be in a drainage pattern until 6'' above the fixture flood rim of the fixtures served (CPC 905.3)
Hangers not to abrade pipe (no metal straps in contact) (IS 5&9)
Support to resist sagging & distortion or upward thrust (CPC 314.2)
Hangers and support spacing as per Table 3-2 CPC (CPC 314.0)
Allow for thermal expansion & contraction ( IS 5&9)
Rain water shall not connect to sanitary system (CPC 714.2)
Size according to DFU load (CPC 703.1)
Vertical to horizontal or horizontal to horizontal through wye branches or 45° wye branches or equivalent (drainage pattern) (CPC 706.3 & 4)
Sanitary tee OK only for horizontal to vertical (CPC 706.2)
Double sanitary tee OK if barrel of fitting is 2 pipe sizes larger than inlets (CPC 706.2)
No flat venting (takeoff above horizontal centerline) (CPC 905.3)
Horizontal vent min 6in above fixture flood rim of fixture (CPC 905.3)
Vent opening above weir (toilet excepted) (CPC 905.5)
Fire blocking around ceiling/floor plate penetrations (CPC 1501.0)
Steel plate if <1-1/2in {1in UPC} from framing edge (CPC 313.9)
Tailpiece max vertical distance 24in except clothes washer 30in (CPC 1001.4)
Horizontal vent min 6in above fixture flood rim of fixture (CPC 905.3)
| LAUNDRY | Standpipe min 18in max 30" above trap (CPC 804.1)
Trap min 6in max 18in above floor (CPC 804.1)
|  | Laundry tub may drain to standpipe within 30in (LOCAL) | INFORMATION ONLY
Provide a minimum 2" drain (CPC Table 7-3 (2))
No trap below floor (CPC 804.1)
RP31 | RP31 GAS | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
Main shutoff required outdoors at each building (CPC 1211.11.3)
Material: steel (galv or black), type K or L Cu, CSST (CPC 1209.5.3.2)
Interior of pipe or tubing must be deburred (CPC 1209.5.5)
Size pipe per tables, provide sizing layout and calcs as required (CPC 1209.5.3.2)
Support per tables and CPC 1211.2.6 (CPC 314.1 & 1211.2.6)
No unions or bushings in concealed locations, Unions only allowed at appliance connections with valve (CPC 1211.3.2 and Oakland Amendments)
|  | CSST Gas piping requires certified installer, provide pocket certifications as required by manufacturer | INFORMATION ONLY
RP32 | RP32 WATER | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
Min water service 3/4in (CPC 610.8)
Size according to H20 fixture units, pressure and elevation (CPC 610.0)
No reduction to inlet of service by softener, backflow (CPC 610.2)
Support per tables and/or manufacturers installation requirements. (CPC 314.1)
Excessive pressure >80psi must be regulated (CPC 608.2)
|  | Use of plastic domestic water piping has additional installation requirements as noted in the Plumbing code. Maintain manufacturers installation quides on site and install per manufacturers and 2010 CPC requirements. | INFORMATION ONLY
Water pipe test 15 minutes w/ potable water at working pressure or 50psig air for nonplastic pipe only (CPC 609.4)
Isolate copper lines from contact with dissimilar metals (CPC 316.2.4)
Burred ends of pipe and tubing shall be reamed to the full bore of the pipe or tube (CPC 310.3)
RP33 | RP33 TUB / SHOWER PAN
| SHOWER PAN | Approved Plans on site (CPC 103.3.2) | INFORMATION ONLY
Shower walls nonabsorbent to min 72 in. above drain (CPC IS-4.6}
|  | Diameter is measured to center of threshold (CPC 411.7) | INFORMATION ONLY
Min area 1024 sq. in. & min diameter 30 in. measured from finished wall (CPC 411.7)
Curb min 2in & max 9in (CPC 411.6)
Finished threshold height min 1 in. below rest of shower receptor & 2–9 in. above top of drain (CPC 411.6)
Door min 22 in. wide (CPC 411.6)
Door must open outward (CPC 411.6)
Secure shower valve, head/riser to permanent structure (CPC 411.11)
Listed anti-scald/pressure balance valve req’d 120˚F max (CPC 418.0)
Slope underlayment ¼ in./ft. (CPC 411.8)
Liner min 3 in. above dam (CPC 411.8)
Pan liner plastic or 3 layers hot mop type 15 felt. Liner to be approved and listed as used (CPC 411.8)
Weep holes at drain req’d & must remain clear (CPC 411.8)
No fasteners < 1 in. above finished threshold (CPC 411.8)
Roll over top of rough threshold (no penetrations through top) & fasten to outside edge (CPC 411.8)
Outside dimensions: IAPMO listed—39½ in. Min rough pan (34in×34in CPC)
Provide for test and inspection of shower pan and/or membrane after installation per requirements of CPC 411.8 (CPC 411.8.1)
| TUB | An access opening at least 12 in. x 12 in. is required for concealed slip joints (CPC 404.2)
Over-rim bath spout—min air gap 2 in. from FLR (CPC T6-3)
Tub or whirlpool max water temperature 120ºF (CPC 414.5)
Whirlpool tub pump requires removable access panel (CPC 414.1)
|  | Tub and showers require testing and inspection (CPC 411.8.1) | INFORMATION ONLY
Tub waste openings shall be protected by the installation of approved metal collars or metal screen fastened to the structure with no opening exceeding one-half (1/2) inch (CPC 313.12.4)
| NOTCHING / BORING | Steel-plate protection for pipes other than galvanized & cast iron in notches or holes < 1½ in. (1 in. UPC) of face of framing (CPC 313.9)
Protection min 2 in. above sole plates & below top plates
Protection min 1½ in. beyond outside of pipe (CPC 313.9*)
Protective plates min 18 gage (CPC 313.9)
Drilling & notching per T34, (CPC 313.2)
Notching 25% max in bearing wall, 40% nonbearing (CPC 602.6)
Bored holes min 5/8 in. from face of stud (CPC 602.6)
Boring 40% max in bearing wall, 60% nonbearing EXC F71, (CPC 602.6)
• 2 successive doubled bearing studs 60% OK F71 (CPC 602.6)
If top plate > 50% removed for pipes, attach galvanized 16-gage metal tie 1½ in. wide with min 8-10d nails each side of notch EXC (CPC 602.6.1)
RP34 | RP34 ANTI-SIPHON VALVE | Atmospheric vacuum breakers OK for: Hose connections (not needed for tank drain valves) (CPC 603.4.7)
Irrigation system, 6 in. above highest head F63 (CPC T6-2)
Integral air gaps in fixtures to recognized standards OK for: Pullout spouts & sprayers with integral backflow AMI (CPC 603.3.7). Pull-out or separate shower spray wands (CPC 603.3.7)
RP38 | RP38 OK TO CONCEAL | OK to cover per Plumbing pending Bldg/Elec/Mech
RP40 | RP40 WATER SERVICE | Min water service 3/4in (CPC 610.8)
Water service material may be any material referenced in CPC table 6-4 and installed according to its listing
Any non-metallic water service shall be accompanied by a 18 awg blue tracer wire exposed at both ends (CPC 604.8 exc)
size according to H20 fixture units, pressure and elevation
No reduction to inlet of service by softener, backflow (CPC 610.2)
Accessible full-bore main shutoff required (CPC 605.2)
Excessive pressure >80psi must be regulated (CPC 608.2)
Expansion tank required for regulators w/o integral bypass & for building supplies w/ check valves (CPC 608.2&3)
Backflow protection from fire sprinkler piping w/ fire department connection or w/ additives or antifreeze (CPC 603.4.16)
RP41 | RP41 GAS TEST | Drip legs at low points if water vapor in gas (CPC 1211.8.1)
Gas pipe not OK as grounding electrode in earth (CPC 1211.15.3)
Electrically bond above-ground metal gas pipes (CPC 1211.15.1)
Appliance EGC sufficient to bond non-CSST gas pipe (CPC 1211.15.1)
Bond CSST where gas service enters building (CPC 1211.15.2)
CSST bonding jumper min 6AWG Cu (CPC 1211.15.2)
Gas pressure test to be done after wall cover, cabinetry, and appliances are installed, and gas system is not subject to damage (CPC 1204.3.2)
|  | Test pressure to be accomplished by the installer using a test guage no greater than 3 times the test pressure and showing 1 PSI increments. Test pressure to be 10 PSI for a duration of 15 min with no loss of pressure (Oakland Amendments) | INFORMATION ONLY
RP42 | RP42 UTILITY RELEASE | Release to PG&E for meter set only after gas piping rough inspection, final gas test, verification that gas appliances/equipment are safe to light per venting, seismic, and safety valve installations, and approval by building inspector | INFORMATION ONLY
RP43A | RP43A ENERGY CODE | Provide original copies of correctly filled out CF-6R Installation Certificate forms for the field inspector at or prior to the final inspection. | INFORMATION ONLY
|  | Required Energy Efficiency Standards Compliance Forms (2008 EES): | INFORMATION ONLY
|  | Domestic Hot Water (DHW) CF-6R-MECH-01 | INFORMATION ONLY
|  | Solar Domestic Hot Water Systems (SDHW) CF-6R-MECH-02 | INFORMATION ONLY
RP43B | RP43B CALGREEN | Indoor water use will be reduced by at least 20% using one of the following methods per CGC 4.303.1
(A) Water saving fixtures for flow restrictors are used and listing on plan per CGC Table 4.303.2
(B) A 20% reduction in baseline water used has been calculated in accordance to “Baseline Water Use” worksheet
Water closet(s), faucet(s) and showerhead(s) have all required standards listed on plans and are in accordance to CGC Table 4.303.3
Automatic irrigation system controller, if provided, will be weather based per CGC 4.304.1
Any gas fireplaces will be a direct-vent sealed-combustible type.
• Install only a direct-vent sealed-combustion gas or sealed wood-burning fireplace or a sealed woodstove & refer to residential requirements in the California Energy Code, Title 24, Part 6, Subchapter 7, Section 150. Woodstoves. Woodstoves shall comply with US EPA Phase II emission limits.
RP44 | RP44 CHLORINATION | New or repaired potable water systems shall be disinfected prior to use whenever required by the Authority Having Jurisdiction (AHJ). The approved method for flushing and/or disinfection as described by CPC Sections 609.9.1 through 609.9.4 (CPC 609.9) | INFORMATION ONLY
|  | Provide copy of sterilization/test report to building inspector prior to occupancy (LOCAL) | INFORMATION ONLY
RP86 | FINAL PLUMBING
| Appliance Shutoffs & Connections | Shutoff valve ahead of union & <=6ft of appliance EXC (CPC 1212.5)
Max length connector 6ft (CPC 1212.5)
Flex connectors completely in same room as appliance (CPC 1212.1)
|  | Connector not through appliance housing EXC | INFORMATION ONLY
Sediment trap close as practical to appliance EXC (CPC 1212.7)
| Fixtures | Individual shutoff (may be at manifold) required for each fixture or appliance except tubs & showers (CPC 605.5)
Fixtures smooth, impervious & free from concealed fouling areas (CPC 401.1)
Joint between fixtures & walls or floors sealed (CPC 407.2)
| Toilet / Bidet | 15 in min side clearance from center (CPC 407.6)
Provide a 24in min clearance in front of toilet (CPC 407.6)
Flange secured to floor & corrosion-resistant fasteners (CPC 407.3)
Max 1.6 gallons per flush (CPC 402.2)
Max discharge temp at bidet 110°F with approved tempering device ASSE 1070 (CPC 416.3)
| Tubs | Min 12×12in access required to slip joint connections F37 (CPC 404.2)
The maximum temperature of hot water discharging from the bathtub and/or whirlpool filler shall be limited to 1200F by a device that conforms to ASSE 1070 or CSA B125.3. The water heater thermostat shall not be considered a control for meeting this provision (CPC 414.5)
Over-rim bath faucet–min vertical air gap 2in (CPC T6-3)
Tub hose attachments req vacuum breaker (CPC 603.4.7)
Whirlpool tub pump requires removable access panel (CPC 414.1)
Min opening 12×12in, 18×18in if pump >2ft from opening (CPC 414.1 and LOCAL)
|  | Whirlpool tub leak testing & pump operation AMI | INFORMATION ONLY
| Showers | Min stall area {1,024sq.in CPC} to 70in high (CPC 411.7)
Min rough pan {34in×34in CPC} (CPC 411.7)
|  | Min 24in clearance in front of shower opening (LOCAL) | INFORMATION ONLY
Door must open outward, min 22in wide (CPC 411.6)
Nonabsorbent surface [to 72in above floor in IRC] (CPC 401.1)
Shower head not to discharge at shower entrance (CPC 411.10)
Individual pressure balance valve required 120°F max (CPC 418.0)
| Kitchen | Dishwasher drain through wye fitting or to disposer head (CPC 404.4)
Air gap device above FLR required for Dishwasher drain (CPC 807.4)
| Water Heaters | Full-open valve required on cold water supply (CPC 605.2)
Unions required within 12in for service and removal (CPC 609.5)
Electric WH requires in-sight or lockable disconnect {see Electrical Appliances: Required Disconnecting Means}
Fuel-fired WH prohibited in storage closets (LOCAL)
Fuel-fired WH prohibited in bedroom, bathroom, or their closets EXC (CPC 505.1)
Watertight pan required if leaks would cause damage (CPC 508.4)
Ignition source >=18in above garage floor EXC (CPC 508.14)
Protection from vehicles required in garage (CPC 508.14)
Seismic restraint upper & lower 1/3rd of tank (CPC 508.2)
Min 30in working space in front (UMC)
Min closet door size 24in wide (UMC)
Attic: solid passage floor max 20ft, min 24in wide (CPC 509.4)
Attic equipment requires light and receptacle near WH (CPC 509.4.5)
| TPR Safety Valve | Combination TPRV required in CPC (CPC 608.3)
Size at least same as outlet & serve only one valve (CPC 608.5)
t&P cannot terminate in overflow pan (CPC 508.5)
6–24in CPC from ground, floor, or receptor (CPC 608.5)
Watts 210 also requires pressure-relief valve (CPC 505.6)
| Vents & Flues | Draft hood /barometric damper in same space as WH (510.12.5)
Terminate min 5ft above draft hood (510.6.2.1)
Only 1 draft hood (510.12.3)
Secure vent connector to draft hood & vent w/screws or other approved means (CPC 510.10.7)
Single wall metal pipe shall not be used as a vent in dwellings and residential occupancies (NFPA 54-09 & CMC 802.7.4.1)
No single-wall in concealed space or attic (CMC 802.7.4.3)
No single-wall outdoors in cold climate (CMC 802.7.2)
| Condensing Appliances | Show direct vent appliance vent termination with clearances specified by manufacturers installation instructions (AMI), submit manufacturers installation documents, etc. (CMC 802.1.1 & 802.2 & 3)
Provide manufacturers listing instructions showing the venting criteria and condensate waste disposal for condensing appliances (CMC 802.4, 802.8, 802.8.5, and 802.9)
Show category of appliance venting, ex: l, ll, lll, lV and verify materials used for venting meet listings as indicated in AMI, Many manufacturers do not allow cellular core ABS or PVC pipe to be used as venting materials (CMC 802.4.3, 802.4, Table 8.1, AMI)
| General | No removable vacuum breakers on all hose faucets (CPC 603.4.7)
Backflow protection on irrigation systems (CPC 603.4.6.1)
Vacuum breaker {6in CPC} above sprinkler heads (CPC T6-2)
No valves downstream of vacuum breaker (CPC IS8:2.4.4)
{WH supported on ground requires 3in concrete base – CPC
Outdoor enclosure required unless WH listed for outdoors (CPC 508.27)
|  | Provide Pex / CPVC water piping certification that meet the flushing and tagging procedures listed in CPC §604 (CPC 604) | INFORMATION ONLY
Water pressure regulator required when water pressure exceeds 80 PSI. and shall be approved type with an adequate strainer (CPC 608.2)
Clean outs: install cleanouts within 2’ feet of building and extended to grade with approved fittings. (CPC 715.1 & 719)
Gas meters, valves, and equipment are protected from damage (CPC 313.3)
Gas appliances shall be protected from vehicular traffic with bollards (i.e. gas water heater, furnace, dryer) (CPC 508.14 & CMC 307)
Water closet spaces shall be at least 30 inches wide; 15” min. from wall to center of W/C with at least 24 inches clear in front of the W/C. (CPC 407.5)
Water closet base caulked at floor. All new water closets shall be 1.6 gallon per flush maximum (CPC 407.2)
R-4 Insulation first 5’ hot and cold water pipe. 2008 EES 150(J) If a recirculation pump is installed the entire hot water system must be insulated. Exception: piping located in the attic that is continuously buried by at least 4” of insulation CEC
|  | Tankless water heater shall be installed per manufacturer’s installation instructions. Requires ¾” dedicated gas line (no other appliances on branch) (Manual shall be available for inspector during inspection). Gas calculations required. | INFORMATION ONLY
|  | Tankless water heater shall be independently vented with a category III (Stainless steel) venting system. Verify clearances to combustibles | INFORMATION ONLY
| AC Compressor | A/C compressors shall be indicated and located per approved site plan. | INFORMATION ONLY
Disconnect shall be readily accessible and not more than 6’-7” above grade. (do not install disconnect behind unit.) CEC §440.14
Secure A/C unit to platform. (CMC 303.6)
Verify that circuit breaker &/or fuse are sized per name plate. CEC §440.4 (B)
Verify that an accessible electrical receptacle is installed at the same level and within 25’ of the A/C unit. The outlet shall not be connected to the load side of the A/C disconnect. CEC §210.63
|  | Not within 5’ from any property line. Verify approved location by zoning. (LOCAL) | INFORMATION ONLY
| DOCUMENTATION | Provide copy of sterilization/test report to building inspector prior to occupancy (LOCAL) | INFORMATION ONLY
|  | If new testable backflow devices have been install on the domestic water supply - provide the building inspector a copy of test report by an approved 3rd party tester as well as the required copy to EBMUD (LOCAL) | INFORMATION ONLY
|  | Provide original copies of correctly filled out CF-6R Installation Certificate forms for the field inspector at or prior to the final inspection. | INFORMATION ONLY
|  | Required Energy Efficiency Standards Compliance Forms (2008 EES): | INFORMATION ONLY
|  | Domestic Hot Water (DHW) CF-6R-MECH-01 | INFORMATION ONLY
|  | Solar Domestic Hot Water Systems (SDHW) CF-6R-MECH-02 | INFORMATION ONLY
| FINAL PLUMBING | OK to occupy pending Bldg/Elec/Plbg