## Standard Method
STANDARD METHOD
APPLIANCES |  |  |  | BTU'S
WATER HEATER |  |  |  | 200000
FURNACE
POOL HEATER
SPACE HEATER
OTHER
OTHER
|  |  |  | LENGTH |  | WIDTH |  | HEIGHT
ROOM DIMENSIONS |  |  |  | 10 | x | 10 | x | 8
COMMUNICATING ROOMS |  |  |  | 10 |  | 10 |  | 10
COMMUNICATING ROOMS
|  | ROOM VOLUME: |  | 1800
|  | TOTAL BTU'S: |  | 200000
|  | MAX BTU INPUT: |  | 36000
|  | OPENINGS REQ: |  | YES
*One duct commencing within 12" of the top, and one commencing within 12" of the bottom. Must communicate directly with the outdoors.
Square Inches Req: |  | 50
Metal Louvers: |  | 62.5 | sq. in. |  | Opening: | 7.9057 | X | 7.9057
| Wood Louvers: | 87.5 | sq. in. |  | Opening: | 9.3541 | X | 9.3541
REDUCED OPENINGS
required volume |  | 10000
percentage available |  | 0.18
required opening |  | 50
percent required |  | 0.82
area required |  | 41
Square Inches Req: |  | 41
Metal Louvers: |  | 51.25 | sq. in. |  | Opening: | 7.1589 | X | 7.1589
Wood Louvers: |  | 71.75 | sq. in. |  | Opening: | 8.4705 | X | 8.4705
* Minimum dimensions of air openings no less than 3".
*Ref: NFPA 54 Fuel Gas Code Handbook, 2006 | [7 empty] | LauraBiggie/2008

## One Opening
ONE OPENING
APPLIANCES |  | BTU'S PER HOUR
WATER HEATER |  | 200000
FURNACE |  | 0
POOL HEATER |  | 0
SPACE HEATER |  | 0
OTHER |  | 0
OTHER |  | 0
*Appliances must have 1" clearance from the back and sides, 6" minimum clearance in front.
| TOTAL BTU'S: | 200000
Square Inches Req: | 66.6667
Metal Louvers: | 83.3333 | sq. in. | Opening: | 9.1287 | X | 9.1287
Wood Louvers: | 116.6667 | sq. in. | Opening: | 10.8012 | X | 10.8012
*Opening must be no less than the sum of the area of all vent connectors.
VENT SIZE
3
4
|  |  | Total: | 19.635
* Minimum dimensions of air openings no less than 3".
*Ref: NFPA 54 Fuel Gas Code Handbook, 2006 |  |  |  |  | LauraBiggie/2008

## Two Openings
TWO OPENINGS
APPLIANCES |  |  |  | BTU'S PER HOUR
WATER HEATER |  |  |  | 200000
FURNACE |  |  |  | 0
POOL HEATER |  |  |  | 0
SPACE HEATER |  |  |  | 0
OTHER |  |  |  | 0
OTHER |  |  |  | 0
|  | TOTAL BTU'S: |  | 200000
SQ. IN. REQUIRED
Vertical Duct: |  | 50 |  | *One duct commencing within 12" of the top, and one commencing within 12" of the bottom.
Horizontal Duct: |  | 100
Area of Square Duct |  | Area of Round Duct |  |  | AREA CALCULATOR
Side In. | Area | Diameter | Area
3 | 9 | 3 | 7.1
4 | 16 | 4 | 12.6 |  | Length: | 4
5 | 25 | 5 | 19.6 |  | Width: | 4
6 | 36 | 6 | 28.3 |  | Sq. In.: | 16
7 | 49 | 7 | 38.5
8 | 64 | 8 | 50.2 |  | Diameter: | 3
10 | 100 | 10 | 78.5 |  | Sq. In. | 7.0686
12 | 144 | 12 | 113
14 | 196 | 14 | 153.9
16 | 256 | 16 | 201
*Ref: NFPA 54 Fuel Gas Code Handbook, 2006 | [5 empty] | LauraBiggie/2008

## Combining Spaces
COMBINING SPACES
APPLIANCES |  |  | BTU'S PER HOUR
WATER HEATER |  |  | 200000
FURNACE |  |  | 0
POOL HEATER |  |  | 0
SPACE HEATER |  |  | 0
OTHER |  |  | 0
OTHER |  |  | 0
| TOTAL BTU'S: |  | 200000
|  |  | LENGTH |  | WIDTH |  | HEIGHT
ROOM DIMENSIONS |  |  | 10 | x | 10 | x | 8
COMMUNICATING ROOMS |  |  | 10 |  | 10 |  | 10
COMMUNICATING ROOMS |  |  | 0 |  | 0 |  | 0
| ROOM VOLUME: |  | 1800
| REQUIRED VOLUME: |  | 10000
| VOLUME ADEQUATE: |  | NO
DIFFERENT STORIES
*One or more openings having a total of:
Square inches req: | 400
Metal Louvers: | 500 | sq. in. |  | Opening: | 22.3607 | X | 22.3607
Wood Louvers: | 700 | sq. in. |  | Opening: | 26.4575 | X | 26.4575
SAME STORY
*EACH opening no < 100 sq. in. (top and bottom):
Square inches req: | 200
Metal Louvers: | 250 | sq. in. |  | Opening: | 15.8114 | X | 15.8114
Wood Louvers: | 350 | sq. in. |  | Opening: | 18.7083 | X | 18.7083
*Ref: NFPA 54 Fuel Gas Code Handbook, 2006 |  |  |  |  | LauraBiggie/2008

## KAIR
KAIR METHOD
|  |  |  | LENGTH |  | WIDTH |  | HEIGHT
ROOM DIMENSIONS |  |  |  | 10 | x | 10 | x | 8
COMMUNICATING ROOMS |  |  |  | 10 |  | 10 |  | 10
COMMUNICATING ROOMS |  |  |  | 0 |  | 0 |  | 0
|  | ROOM VOLUME: |  | 1800 |  | Cu. Ft.
NON-FAN ASSISTED APPLIANCES
APPLIANCES |  |  |  | BTU'S PER HOUR
WATER HEATER |  |  |  | 40000
FURNACE
POOL HEATER
SPACE HEATER
OTHER
OTHER
|  | TOTAL BTU'S: |  | 40000
|  | KAIR: |  | 0.5
| REQUIRED VOLUME: |  |  | 1680 | Cu. Ft.
FAN ASSISTED APPLIANCES
APPLIANCES |  |  |  | BTU'S PER HOUR
WATER HEATER |  |  |  | 100000
FURNACE
POOL HEATER
SPACE HEATER
OTHER
OTHER
|  | TOTAL BTU'S: |  | 100000
|  | KAIR: |  | 0.5
| REQUIRED VOLUME: |  |  | 3000 | Cu. Ft.
| TOTAL REQUIRED VOLUME: |  |  | 4680 |  | Cu. Ft.
ADDITIONAL OPENINGS REQUIRED: |  |  |  | YES
*Ref: NFPA 54 Fuel Gas Code Handbook, 2006 | [5 empty] | LauraBiggie/2008