## Sheet1
Hazen-Williams Friction (Pressure Loss) Calculator
Input
Actual pipe diameter (in): | 2.067
Friction coefficient: | 140
Flow rate (gpm): | 22
Length of pipe (ft): | 100
Output
Pressure loss (ft): | 0.98866
Pressure Loss (psi): | 0.42512
Table 1. Pipe inner diameter of various pipe specifications (Uni-Bell, 2001)
Nominal diameter (in) | Inner diameter in inches
| Sch 40 | Sch 80 | SDR 26 | SDR 21 | SDR 13.5 | (API) Flexible PVC
½ | 0.622 | 0.546 |  |  | 0.716 | 0.546
| 0.824 | 0.742 |  |  | 0.894 | 0.74
1 | 1.049 | 0.957 | 1.195 |  | 1.121 | 0.96
1 ¼ | 1.38 | 1.278 | 1.532 | 1.502 | 1.414
1 ½ | 1.61 | 1.5 | 1.754 | 1.72 | 1.618
2 | 2.067 | 1.939 | 2.193 | 2.149 | 2.023
2.5 | 2.469 | 2.323 | 2.655 | 2.601 | 2.449
3 | 3.068 | 2.9 | 3.23 | 3.166 | 2.982
3 ½ | 3.548 | 3.364 | ----- | 3.62 | 3.408
4 | 4.026 | .3.826 | 4.154 | 4.072 | 3.834
Table 2. Equivalent pipe length of common fittings (CIDWT, 2008)
Diameter of fitting (in) | 90. Degree Standard Ell | 45 Degree Standard Ell | 90 Degree Standard Tee | coupling or Straight Run Of Tee | Gate Valve | Globe Valve | Check Valve
Equivalent Pipe Length (ft)
3/8 | 1 | 0.6 | 1.5 | 0.3 | 0.2 | 8 | 3
1/2 | 2 | 1.2 | 3 | 0.6 | 0.4 | 15 | 5
3/4 | 2.5 | 1.5 | 4 | 0.8 | 0.5 | 20 | 7
1 | 3 | 1.8 | 5 | 0.9 | 0.6 | 25 | 8
1.25 | 4 | 2.4 | 6 | 1.2 | 0.8 | 35 | 11
1.5 | 5 | 3 | 7 | 1.5 | 1 | 45 | 14
2 | 7 | 4 | 10 | 2 | 1.3 | 55 | 19
2.5 | 8 | 5 | 12 | 2.5 | 1.6 | 65 | 22
3 | 10 | 6 | 15 | 3 | 2 | 80 | 27
3.5 | 12 | 7 | 18 | 3.6 | 2.4 | 100 | 32
4 | 14 | 8 | 21 | 4 | 2.7 | 125 | 38
5 | 17 | 10 | 25 | 5 | 3.3 | 140 | 46
6 | 20 | 12 | 30 | 6 | 4 | 165 | 54
References
CIDWT. 2008. Installation of Wastewater Treatment Systems. Consortium of institutes for Decentralized Wastewater Treatment. Pilot Test Version 2. March 2008.
Uni-Bell. 2001. Handbook of PVC Pipe. Dallas, TX. Uni-Bell PVC Pipe Association