## Calcs
WATER AND WASTE SERVICE CALCULATIONS
JOB NAME: | [6 empty] | DATE: | 2026-07-29
FIXTURE TYPE | NO. | WASTE |  | COLD WATER |  | HOT WATER |  | TOTAL WATER
|  | FU | TOTAL | FU | TOTAL | FU | TOTAL | FU
BAR SINK |  | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 0
BATH TUB/SHOWER |  | 3 | 0 | 3 | 0 | 3 | 0 | 0
CLOTHES WASHER |  | 3 | 0 | 3 | 0 | 3 | 0 | 0
DRINKING FOUNTAIN |  | 0.5 | 0 | 0.5 | 0 | 0 | 0 | 0
HOSE BIBB |  | 0 | 0 | 2.5 | 0 | 0 | 0 | 0
KITCHEN SINK (DOMESTIC) |  | 3 | 0 | 1.125 | 0 | 1.125 | 0 | 0
LAUNDRY SINK |  | 2 | 0 | 1.125 | 0 | 1.125 | 0 | 0
LAVATORY (SINGLE) |  | 1 | 0 | 0.75 | 0 | 0.75 | 0 | 0
LAVATORY (MULTIPLE) |  | 2 | 0 | 0.75 | 0 | 0.75 | 0 | 0
SERVICE SINK |  | 3 | 0 | 2.25 | 0 | 2.25 | 0 | 0
FLOOR DRAIN |  | 2 | 0 | 0 | 0 | 0 | 0 | 0
FLOOR SINK RECEPTOR |  | 3 | 0 | 0 | 0 | 0 | 0 | 0
SHOWER |  | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 0
SINK, 1-1/2" TRAP |  | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 0
SINK, 2" TRAP |  | 3 | 0 | 1.5 | 0 | 1.5 | 0 | 0
URINAL, 1.0 GPF |  | 4 | 0 | 4 | 0 | 0 | 0 | 0
WASHFOUNTAIN, 1-1/2" |  | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 0
WATER CLOSET, 1.6 TANK |  | 4 | 0 | 2.5 | 0 | 0 | 0 | 0
WATER CLOSET, 1.6 FV |  | 4 | 0 | 5 | 0 | 0 | 0 | 0
MISCELLANEOUS FIXTURE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MISCELLANEOUS FIXTURE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MISCELLANEOUS FIXTURE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL FU |  |  | 0 |  | 0 |  | 0 | 0
EQUIVALENT COLD WATER FLOW RATE (GPM): | [5 empty] | #N/A |  |  |  | 20.36
ADDITIONAL DEMAND LOAD (GPM)
PRESSURE AVAILABLE AT MAIN (PSI):
PRESSURE BOOSTER PUMP | [8 empty] | 0 | MINIMUM REQUIRED PRESSURE BOOST VALUE (PSI)
MINIMUM REQUIRED FIXTURE PRESSURE (PSI):
ELEVATION RISE (FT):
METER LOSS (PSI):
BACKFLOW PREVENTER LOSS (PSI):
ADDITIONAL LOSSES (PSI):
EQUIVALENT PIPE LENGTH FROM METER TO MOST REMOTE FIXTURE (FT):
FRICTION LOSS PRESSURE AVAILABLE (PSI): | [5 empty] | 0
MAXIMUM ALLOWABLE FRICTION LOSS (PSI/100 FT): | [5 empty] | #DIV/0!
WATER FLOW VELOCITY (FPS): | [5 empty] | #N/A
CALCULATED FRICTION HEAD LOSS (PSI/100 FT): | [5 empty] | #N/A
MINIMUM REQUIRED 'WATER' PIPE SIZE (INCHES): | [5 empty] | #N/A
MINIMUM REQUIRED 'WASTE' PIPE SIZE (INCHES): | [5 empty] | 2
(CALCULATIONS PER THE UPC/CPC)
HIDE & CHECK
RESET
COPY TO CLIPBOARD

## WATER SIZE CHART - Cu L
WATER PIPE SIZING CHART
PIPE SIZES CALCULATED BASED ON UPC/CPC APPENDIX A
SIZE: TYPE L COPPER |  | CW MAX FLOW |  | CW FIXTURE UNIT VALUES |  | HW MAX FLOW |  | HWFU
NOMINAL DIAMETER | INTERNAL DIAMETER | GPM | FPS | FLUSH TANK | FLUSH VALVE | GPM | FPS | HOT WATER
3/8" | 0.44 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1/2" | 0.545 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3/4" | 0.785 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1" | 1.025 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1-1/4" | 1.265 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1-1/2" | 1.505 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2" | 1.985 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2-1/2" | 2.465 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3" | 2.945 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4" | 3.905 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
5" | 4.875 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
6" | 5.845 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8" | 7.725 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
10" | 9.625 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Constant | 130
CW Max Vel | 8
HW Max Vel | 5
THIS TABLE IS TO BE USED FOR SIZING BRANCH PIPING WITH MORE THAN ONE (1) FIXTURE ONLY. REFER TO THE PLUMBING FIXTURE SCHEDULE FOR INDIVIDUAL FIXTURE BRANCH SIZE.
| GPM | FPS
3/8" | #DIV/0! | #DIV/0!
1/2" | #DIV/0! | #DIV/0!
3/4" | #DIV/0! | #DIV/0!
1" | #DIV/0! | #DIV/0!
1-1/4" | #DIV/0! | #DIV/0!
1-1/2" | #DIV/0! | #DIV/0!
2" | #DIV/0! | #DIV/0!
2-1/2" | #DIV/0! | #DIV/0!
3" | #DIV/0! | #DIV/0!
4" | #DIV/0! | #DIV/0!
5" | #DIV/0! | #DIV/0!
6" | #DIV/0! | #DIV/0!
8" | #DIV/0! | #DIV/0!
10" | #DIV/0! | #DIV/0!

## WATER SIZE CHART - CPVC
WATER PIPE SIZING CHART
PIPE SIZES CALCULATED BASED ON UPC/CPC APPENDIX A
SIZE: TYPE L COPPER |  | CW MAX FLOW |  | CW FIXTURE UNIT VALUES |  | HW MAX FLOW |  | HWFU
NOMINAL DIAMETER | INTERNAL DIAMETER | GPM | FPS | FLUSH TANK | FLUSH VALVE | GPM | FPS | HOT WATER
3/8" | 0.44 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1/2" | 0.545 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3/4" | 0.785 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1" | 1.025 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1-1/4" | 1.265 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1-1/2" | 1.505 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2" | 1.985 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2-1/2" | 2.465 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3" | 2.945 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4" | 3.905 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
5" | 4.875 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
6" | 5.845 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8" | 7.725 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
10" | 9.625 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Constant | 130
CW Max Vel | 8
HW Max Vel | 5
THIS TABLE IS TO BE USED FOR SIZING BRANCH PIPING WITH MORE THAN ONE (1) FIXTURE ONLY. REFER TO THE PLUMBING FIXTURE SCHEDULE FOR INDIVIDUAL FIXTURE BRANCH SIZE.
| GPM | FPS
3/8" | #DIV/0! | #DIV/0!
1/2" | #DIV/0! | #DIV/0!
3/4" | #DIV/0! | #DIV/0!
1" | #DIV/0! | #DIV/0!
1-1/4" | #DIV/0! | #DIV/0!
1-1/2" | #DIV/0! | #DIV/0!
2" | #DIV/0! | #DIV/0!
2-1/2" | #DIV/0! | #DIV/0!
3" | #DIV/0! | #DIV/0!
4" | #DIV/0! | #DIV/0!
5" | #DIV/0! | #DIV/0!
6" | #DIV/0! | #DIV/0!
8" | #DIV/0! | #DIV/0!
10" | #DIV/0! | #DIV/0!

## WATER SIZE CHART - PEX
WATER PIPE SIZING CHART
PIPE SIZES CALCULATED BASED ON UPC/CPC APPENDIX A
SIZE: TYPE L COPPER |  | CW MAX FLOW |  | CW FIXTURE UNIT VALUES |  | HW MAX FLOW |  | HWFU
NOMINAL DIAMETER | INTERNAL DIAMETER | GPM | FPS | FLUSH TANK | FLUSH VALVE | GPM | FPS | HOT WATER
3/8" | 0.44 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1/2" | 0.545 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3/4" | 0.785 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1" | 1.025 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1-1/4" | 1.265 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1-1/2" | 1.505 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2" | 1.985 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2-1/2" | 2.465 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3" | 2.945 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4" | 3.905 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
5" | 4.875 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
6" | 5.845 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8" | 7.725 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
10" | 9.625 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Constant | 130
CW Max Vel | 8
HW Max Vel | 5
THIS TABLE IS TO BE USED FOR SIZING BRANCH PIPING WITH MORE THAN ONE (1) FIXTURE ONLY. REFER TO THE PLUMBING FIXTURE SCHEDULE FOR INDIVIDUAL FIXTURE BRANCH SIZE.
| GPM | FPS
3/8" | #DIV/0! | #DIV/0!
1/2" | #DIV/0! | #DIV/0!
3/4" | #DIV/0! | #DIV/0!
1" | #DIV/0! | #DIV/0!
1-1/4" | #DIV/0! | #DIV/0!
1-1/2" | #DIV/0! | #DIV/0!
2" | #DIV/0! | #DIV/0!
2-1/2" | #DIV/0! | #DIV/0!
3" | #DIV/0! | #DIV/0!
4" | #DIV/0! | #DIV/0!
5" | #DIV/0! | #DIV/0!
6" | #DIV/0! | #DIV/0!
8" | #DIV/0! | #DIV/0!
10" | #DIV/0! | #DIV/0!

## NATURAL GAS
NATURAL GAS SIZING TABLE
BASED ON UPC/CPC TABLE 12-8
7"wc PRESSURE
TOTAL PIPE LENGTH (FT)= |  | 10 | 600 FT MAX
PIPE SIZE | MAX. MBH (CFH)
1/2" | 172 |  |  | 172 | 65 | 44 | 25
3/4" | 360 |  |  | 360 | 137 | 92 | 53
1" | 678 |  |  | 678 | 257 | 173 | 99
1-1/4" | 1390 |  |  | 1390 | 528 | 355 | 203
1-1/2" | 2090 |  |  | 2090 | 791 | 532 | 305
2" | 4020 |  |  | 4020 | 1520 | 1020 | 587
2-1/2" | 6400 |  |  | 6400 | 2430 | 1630 | 935
3" | 11300 |  |  | 11300 | 4290 | 2890 | 1650
4" | 23100 |  |  | 23100 | 8760 | 5890 | 3370
NATURAL GAS SIZING TABLE
BASED ON UPC/CPC TABLE 12-9
2 PSI PRESSURE
TOTAL PIPE LENGTH (FT)= |  | 10 | 1300 FT MAX
PIPE SIZE | MAX. MBH (CFH)
1/2" | 1510 |  |  | 1510 | 615 | 414 | 253 | 174 | 139
3/4" | 3040 |  |  | 3040 | 1240 | 836 | 528 | 363 | 292
1" | 5560 |  |  | 5560 | 2270 | 1530 | 945 | 650 | 522
1-1/4" | 11400 |  |  | 11400 | 4660 | 3140 | 1940 | 1330 | 1070
1-1/2" | 17100 |  |  | 17100 | 6980 | 4700 | 2910 | 2000 | 1600
2" | 32900 |  |  | 32900 | 13500 | 9060 | 5600 | 3850 | 3090
2-1/2" | 52500 |  |  | 52500 | 21400 | 14400 | 8920 | 6130 | 4930
3" | 92800 |  |  | 92800 | 37900 | 25500 | 15800 | 10800 | 8710
4" | 189000 |  |  | 189000 | 77300 | 52100 | 32200 | 22100 | 17800

## Water Heating
| Job Title | 0 | [7 empty] | Date | 2026-07-29
| Occupancy Type. | OFFICE
QTY. | FIXTURE TYPE | G.P.H. PER OCCUPANCY TYPE | [8 empty] | G.P.H.
|  | APART | CLUB | GYM | HOSP | HOTEL | INDUST | OFFICE | RESID | SCHOOL
0 | Lavatory/Bidet/Bar Sink | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0
0 | Basins, public lavatory | 4 | 6 | 8 | 6 | 8 | 12 | 6 | 0 | 15 | 0
0 | Bathtubs | 20 | 20 | 30 | 20 | 20 | 0 | 0 | 20 | 0 | 0
0 | Dishwashers | 15 | 100 | 0 | 100 | 150 | 100 | 0 | 15 | 75 | 0
0 | Foot basins | 3 | 3 | 12 | 3 | 3 | 12 | 0 | 3 | 3 | 0
0 | Kitchen sink | 10 | 20 | 0 | 20 | 30 | 20 | 20 | 10 | 20 | 0
0 | Laundry, stationary tubs | 20 | 28 | 0 | 28 | 28 | 0 | 0 | 20 | 0 | 0
0 | Laundry Tray/Sink | 5 | 10 | 0 | 10 | 10 | 0 | 10 | 5 | 10 | 0
0 | Showers | 30 | 150 | 225 | 75 | 75 | 225 | 30 | 30 | 225 | 0
0 | Slop sink | 20 | 20 | 0 | 20 | 30 | 20 | 20 | 15 | 20 | 0
0 | Hydrotherapeutic showers | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
0 | Hubbard baths | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
0 | Leg baths | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
0 | Arm baths | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0
0 | Sitz baths | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0
0 | Continuous-flow baths | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0
0 | Circular wash sinks | 0 | 0 | 0 | 20 | 20 | 30 | 20 | 0 | 30 | 0
0 | Semicircular wash sinks | 0 | 0 | 0 | 10 | 10 | 15 | 10 | 0 | 15 | 0
0 | TOTAL DEMAND | - | - | - | - | - | - | - | - | - | 0
Demand Factor |  | 0.3 | 0.3 | 0.4 | 0.25 | 0.25 | 0.4 | 0.3 | 0.3 | 0.4 | 0.3
Storage Capacity |  | 1.25 | 0.9 | 1 | 0.6 | 0.8 | 1 | 2 | 0.7 | 1 | 2
Base Required: Heating Capacity |  |  |  |  | 0 | GPH |  |  | Water Tempature
Base Required: Storage Capacity |  |  |  |  | 0 | GAL. |  |  | C.W. | 60 | Deg.
[9 empty] | H.W. | 120 | Deg.
Electric Heat Required. |  |  |  |  | 0 | KW
Gas Heat Required. |  |  |  |  | 0 | MBH |  |  | Duration of Peak load
[10 empty] | 2 | HR's
What size Water Heater tank would you like to use? |  |  |  |  | 40 | GAL
Adjusted Gallons Per Hour Recovery |  |  |  |  | -14 | GPH |  |  | W.H. Efficiencies
[10 empty] | 80 | %
Adjusted Electric Heat Required. |  |  |  |  | -2.051 | KW
Adjusted Gas Heat Required. |  |  |  |  | -8.75 | MBH

## VTR
WASTE MAIN |  |  | 2
CROSS SECTIONAL AREA OF WASTE MAIN |  |  | 3.1416
VENT THRU ROOF SIZES
NUMBER | SIZE | CROSS SECTIONAL AREA | TOT AREA
| 1.5 | 1.7671 | 0
| 2 | 3.1416 | 0
| 2.5 | 4.9087 | 0
| 3 | 7.0686 | 0
| 4 | 12.5664 | 0
TOTAL VENT THRU ROOF CROSS SECTIONAL AREA |  |  | 0

## Data
#N/A | #N/A |  |  | 0 | #N/A |  |  | Flush Tank | Flush Valve
| DIA TO | NOMINAL | INTERNAL | FLUSH TANKS |  |  | Flow | Fixt. Units | Flow | Fixt. Units
TEST | 2-1/2 | DIAMETER | DIAMETER | TEST | FU | GPM | GPM | F.T. | GPM | F.V.
[7 empty] | 0 | 0 | 0 | 0
|  |  |  | #DIV/0! | 6 | 5 | 2 | 1 | 0 | 0
#N/A | 0.22 | 0.5 | 0.545 | #DIV/0! | 8 | 6.5 | 3 | 3 | 0 | 0
#N/A | 0.55 | 0.75 | 0.785 | #DIV/0! | 10 | 8 | 4 | 4 | 0 | 0
#N/A | 1.06 | 1.0 | 1.025 | #DIV/0! | 12 | 9 | 5 | 6 | 0 | 0
#N/A | 1.8 | 1.25 | 1.265 | #DIV/0! | 14 | 11 | 6 | 7 | 0 | 0
#N/A | 2.78 | 1.5 | 1.505 | #DIV/0! | 16 | 12 | 7 | 8 | 0 | 0
#N/A | 5.55 | 2 | 1.985 | #DIV/0! | 18 | 13 | 8 | 10 | 0 | 0
#N/A | 9.54 | 2.5 | 2.465 | #DIV/0! | 20 | 14 | 9 | 12 | 0 | 0
#N/A | 14.87 | 3 | 2.945 | #DIV/0! | 25 | 17 | 10 | 13 | 0 | 0
#N/A | 30.13 | 4 | 3.905 | #DIV/0! | 30 | 20 | 11 | 15 | 0 | 0
#N/A | 52.47 | 5 | 4.875 | #DIV/0! | 35 | 23 | 12 | 16 | 0 | 0
#N/A | 82.6 | 6 | 5.845 | #DIV/0! | 40 | 25 | 13 | 18 | 0 | 0
#N/A | 165.86 | 8 | 7.725 | #DIV/0! | 45 | 27 | 14 | 20 | 0 | 0
#N/A | 287.41 | 10 | 9.625 | #DIV/0! | 50 | 29 | 15 | 21 | 0 | 0
|  |  |  | #DIV/0! | 60 | 32 | 16 | 23 | 0 | 0
#N/A | #N/A |  |  | #DIV/0! | 70 | 35 | 17 | 24 | 0 | 0
|  |  |  | #DIV/0! | 80 | 38 | 18 | 26 | 0 | 0
| GPM |  |  | #DIV/0! | 90 | 41 | 19 | 28 | 0 | 0
#DIV/0! | #DIV/0! | 0.5 |  | #DIV/0! | 100 | 44 | 20 | 30 | 0 | 0
#DIV/0! | #DIV/0! | 0.75 |  | #DIV/0! | 120 | 48 | 21 | 32 | 0 | 0
#DIV/0! | #DIV/0! | 1.0 |  | #DIV/0! | 140 | 53 | 22 | 34 | 22 | 5
#DIV/0! | #DIV/0! | 1.25 |  | #DIV/0! | 160 | 57 | 23 | 36 | 23 | 6
#DIV/0! | #DIV/0! | 1.5 |  | #DIV/0! | 180 | 61 | 24 | 39 | 24 | 7
#DIV/0! | #DIV/0! | 2 |  | #DIV/0! | 200 | 65 | 25 | 42 | 25 | 8
#DIV/0! | #DIV/0! | 2.5 |  | #DIV/0! | 225 | 70 | 26 | 44 | 26 | 9
#DIV/0! | #DIV/0! | 3 |  | #DIV/0! | 250 | 75 | 27 | 46 | 27 | 10
#DIV/0! | #DIV/0! | 4 |  | #DIV/0! | 275 | 80 | 28 | 49 | 28 | 11
#DIV/0! | #DIV/0! | 5 |  | #DIV/0! | 300 | 85 | 29 | 51 | 29 | 12
#DIV/0! | #DIV/0! | 6 |  | #DIV/0! | 400 | 105 | 30 | 54 | 30 | 13
#DIV/0! | #DIV/0! | 8 |  | #DIV/0! | 500 | 125 | 31 | 56 | 31 | 14
#DIV/0! | #DIV/0! | 10 |  | #DIV/0! | 750 | 170 | 32 | 58 | 32 | 15
|  |  |  | #DIV/0! | 1000 | 208 | 33 | 60 | 33 | 16
|  |  |  | #DIV/0! | 1250 | 240 | 34 | 63 | 34 | 18
|  |  |  | #DIV/0! | 1500 | 267 | 35 | 66 | 35 | 20
|  |  |  | #DIV/0! | 1750 | 294 | 36 | 69 | 36 | 21
|  |  |  | #DIV/0! | 2000 | 321 | 37 | 74 | 37 | 23
|  |  |  | #DIV/0! | 2250 | 348 | 38 | 78 | 38 | 25
|  |  |  | #DIV/0! | 2500 | 375 | 39 | 83 | 39 | 26
|  |  |  | #DIV/0! | 2750 | 402 | 40 | 86 | 40 | 28
|  |  |  | #DIV/0! | 3000 | 432 | 41 | 90 | 41 | 30
|  |  |  | #DIV/0! | 4000 | 525 | 42 | 95 | 42 | 31
|  |  |  | #DIV/0! | 5000 | 593 | 43 | 99 | 43 | 33
|  |  |  | #DIV/0! | 6000 | 643 | 44 | 103 | 44 | 35
|  |  |  | #DIV/0! | 7000 | 685 | 45 | 107 | 45 | 37
|  |  |  | #DIV/0! | 8000 | 718 | 46 | 111 | 46 | 39
|  |  |  | #DIV/0! | 9000 | 745 | 47 | 115 | 47 | 42
|  |  |  | #DIV/0! | 10000 | 769 | 48 | 119 | 48 | 44
[7 empty] | 49 | 123 | 49 | 46
[7 empty] | 50 | 127 | 50 | 48
[7 empty] | 51 | 130 | 51 | 50
[7 empty] | 52 | 135 | 52 | 52
[7 empty] | 53 | 141 | 53 | 54
[7 empty] | 54 | 146 | 54 | 57
[7 empty] | 55 | 151 | 55 | 60
[7 empty] | 56 | 155 | 56 | 63
[7 empty] | 57 | 160 | 57 | 66
[7 empty] | 58 | 165 | 58 | 69
[7 empty] | 59 | 170 | 59 | 73
[7 empty] | 60 | 175 | 60 | 76
[7 empty] | 61 | 180 | 61 | 79
[7 empty] | 62 | 185 | 62 | 82
[7 empty] | 63 | 190 | 63 | 85
[7 empty] | 64 | 195 | 64 | 88
[7 empty] | 65 | 200 | 65 | 91.5
[7 empty] | 66 | 205 | 66 | 95
[7 empty] | 67 | 210 | 67 | 98.5
[7 empty] | 68 | 215 | 68 | 102
[7 empty] | 69 | 220 | 69 | 105
[7 empty] | 70 | 225 | 70 | 108
[7 empty] | 71 | 230.5 | 71 | 112
[7 empty] | 72 | 236 | 72 | 116
[7 empty] | 73 | 240.5 | 73 | 120
[7 empty] | 74 | 245 | 74 | 124
[7 empty] | 75 | 249.5 | 75 | 128
[7 empty] | 76 | 254 | 76 | 132
[7 empty] | 77 | 259 | 77 | 136
[7 empty] | 78 | 264 | 78 | 140
[7 empty] | 79 | 269.5 | 79 | 144
[7 empty] | 80 | 275 | 80 | 148
[7 empty] | 81 | 279.5 | 81 | 153
[7 empty] | 82 | 284 | 82 | 158
[7 empty] | 83 | 289 | 83 | 163
[7 empty] | 84 | 294 | 84 | 168
[7 empty] | 85 | 299.5 | 85 | 172
[7 empty] | 86 | 305 | 86 | 176
[7 empty] | 87 | 310 | 87 | 181
[7 empty] | 88 | 315 | 88 | 186
[7 empty] | 89 | 320.5 | 89 | 190.5
[7 empty] | 90 | 326 | 90 | 195
[7 empty] | 91 | 331.5 | 91 | 200
[7 empty] | 92 | 337 | 92 | 205
[7 empty] | 93 | 342.5 | 93 | 209.5
[7 empty] | 94 | 348 | 94 | 214
[7 empty] | 95 | 353.5 | 95 | 218.5
[7 empty] | 96 | 359 | 96 | 223
[7 empty] | 97 | 364.5 | 97 | 228.5
[7 empty] | 98 | 370 | 98 | 234
[7 empty] | 99 | 375 | 99 | 239.5
[7 empty] | 100 | 380 | 100 | 245
[7 empty] | 101 | 385.2 | 101 | 250
[7 empty] | 102 | 390.4 | 102 | 255
[7 empty] | 103 | 395.6 | 103 | 260
[7 empty] | 104 | 400.8 | 104 | 265
[7 empty] | 105 | 406 | 105 | 270
[7 empty] | 106 | 411 | 106 | 275
[7 empty] | 107 | 416 | 107 | 280
[7 empty] | 108 | 421 | 108 | 285
[7 empty] | 109 | 426 | 109 | 290
[7 empty] | 110 | 431 | 110 | 295
[7 empty] | 111 | 435.8 | 111 | 301.8
[7 empty] | 112 | 440.6 | 112 | 308.6
[7 empty] | 113 | 445.4 | 113 | 315.4
[7 empty] | 114 | 450.2 | 114 | 322.2
[7 empty] | 115 | 455 | 115 | 329
[7 empty] | 116 | 459.8 | 116 | 336.2
[7 empty] | 117 | 464.6 | 117 | 343.4
[7 empty] | 118 | 469.4 | 118 | 350.6
[7 empty] | 119 | 474.2 | 119 | 357.8
[7 empty] | 120 | 479 | 120 | 365
[7 empty] | 121 | 484.4 | 121 | 371.2
[7 empty] | 122 | 489.8 | 122 | 377.4
[7 empty] | 123 | 495.2 | 123 | 383.6
[7 empty] | 124 | 500.6 | 124 | 389.8
[7 empty] | 125 | 506 | 125 | 396
[7 empty] | 126 | 511.4 | 126 | 402.8
[7 empty] | 127 | 516.8 | 127 | 409.6
[7 empty] | 128 | 522.2 | 128 | 416.4
[7 empty] | 129 | 527.6 | 129 | 423.2
[7 empty] | 130 | 533 | 130 | 430
[7 empty] | 131 | 538.2 | 131 | 436
[7 empty] | 132 | 543.4 | 132 | 442
[7 empty] | 133 | 548.6 | 133 | 448
[7 empty] | 134 | 553.8 | 134 | 454
[7 empty] | 135 | 559 | 135 | 460
[7 empty] | 136 | 564.2 | 136 | 466
[7 empty] | 137 | 569.4 | 137 | 472
[7 empty] | 138 | 574.6 | 138 | 478
[7 empty] | 139 | 579.8 | 139 | 484
[7 empty] | 140 | 585 | 140 | 490
[7 empty] | 141 | 590.2 | 141 | 496.2
[7 empty] | 142 | 595.4 | 142 | 502.4
[7 empty] | 143 | 600.6 | 143 | 508.6
[7 empty] | 144 | 605.8 | 144 | 514.8
[7 empty] | 145 | 611 | 145 | 521
[7 empty] | 146 | 616.4 | 146 | 528.6
[7 empty] | 147 | 621.8 | 147 | 536.2
[7 empty] | 148 | 627.2 | 148 | 543.8
[7 empty] | 149 | 632.6 | 149 | 551.4
[7 empty] | 150 | 638 | 150 | 559
[7 empty] | 151 | 643.4 | 151 | 566.4
[7 empty] | 152 | 648.8 | 152 | 573.8
[7 empty] | 153 | 654.2 | 153 | 581.2
[7 empty] | 154 | 659.6 | 154 | 588.6
[7 empty] | 155 | 665 | 155 | 596
[7 empty] | 156 | 670.4 | 156 | 603
[7 empty] | 157 | 675.8 | 157 | 610
[7 empty] | 158 | 681.2 | 158 | 617
[7 empty] | 159 | 686.6 | 159 | 624
[7 empty] | 160 | 692 | 160 | 631
[7 empty] | 161 | 697.4 | 161 | 638
[7 empty] | 162 | 702.8 | 162 | 645
[7 empty] | 163 | 708.2 | 163 | 652
[7 empty] | 164 | 713.6 | 164 | 659
[7 empty] | 165 | 719 | 165 | 666
[7 empty] | 166 | 724.8 | 166 | 672.8
[7 empty] | 167 | 730.6 | 167 | 679.6
[7 empty] | 168 | 736.4 | 168 | 686.4
[7 empty] | 169 | 742.2 | 169 | 693.2
[7 empty] | 170 | 748 | 170 | 700
[7 empty] | 171 | 754 | 171 | 707.8
[7 empty] | 172 | 760 | 172 | 715.6
[7 empty] | 173 | 766 | 173 | 723.4
[7 empty] | 174 | 772 | 174 | 731.2
[7 empty] | 175 | 778 | 175 | 739
[7 empty] | 176 | 784.2 | 176 | 746.2
[7 empty] | 177 | 790.4 | 177 | 753.4
[7 empty] | 178 | 796.6 | 178 | 760.6
[7 empty] | 179 | 802.8 | 179 | 767.8
[7 empty] | 180 | 809 | 180 | 775
[7 empty] | 181 | 815.2 | 181 | 782.2
[7 empty] | 182 | 821.4 | 182 | 789.4
[7 empty] | 183 | 827.6 | 183 | 796.6
[7 empty] | 184 | 833.8 | 184 | 803.8
[7 empty] | 185 | 840 | 185 | 811
[7 empty] | 186 | 846.8 | 186 | 818.8
[7 empty] | 187 | 853.6 | 187 | 826.6
[7 empty] | 188 | 860.4 | 188 | 834.4
[7 empty] | 189 | 867.2 | 189 | 842.2
[7 empty] | 190 | 874 | 190 | 850
[7 empty] | 191 | 881.1 | 191 | 858.1
[7 empty] | 192 | 888.2 | 192 | 866.2
[7 empty] | 193 | 895.3 | 193 | 874.3
[7 empty] | 194 | 902.4 | 194 | 882.4
[7 empty] | 195 | 909.5 | 195 | 890.5
[7 empty] | 196 | 916.6 | 196 | 898.6
[7 empty] | 197 | 923.7 | 197 | 906.7
[7 empty] | 198 | 930.8 | 198 | 914.8
[7 empty] | 199 | 937.9 | 199 | 922.9
[7 empty] | 200 | 945 | 200 | 931
[7 empty] | 201 | 952.3 | 201 | 938.8
[7 empty] | 202 | 959.6 | 202 | 946.6
[7 empty] | 203 | 966.9 | 203 | 954.4
[7 empty] | 204 | 974.2 | 204 | 962.2
[7 empty] | 205 | 981.5 | 205 | 970
[7 empty] | 206 | 988.8 | 206 | 977.8
[7 empty] | 207 | 996.1 | 207 | 985.6
[7 empty] | 208 | 1003.4 | 208 | 993.4
[7 empty] | 209 | 1010.7 | 209 | 1001.2
[7 empty] | 210 | 1018 | 210 | 1009
[7 empty] | 211 | 1025.3 | 211 | 1017.2
[7 empty] | 212 | 1032.6 | 212 | 1025.4
[7 empty] | 213 | 1039.9 | 213 | 1033.6
[7 empty] | 214 | 1047.2 | 214 | 1041.8
[7 empty] | 215 | 1054.5 | 215 | 1050
[7 empty] | 216 | 1061.8 | 216 | 1058.2
[7 empty] | 217 | 1069.1 | 217 | 1066.4
[7 empty] | 218 | 1076.4 | 218 | 1074.6
[7 empty] | 219 | 1083.7 | 219 | 1082.8
[7 empty] | 220 | 1091 | 220 | 1091
[7 empty] | 221 | 1099.2 | 221 | 1099.2
[7 empty] | 222 | 1107.4 | 222 | 1107.4
[7 empty] | 223 | 1115.6 | 223 | 1115.6
[7 empty] | 224 | 1123.8 | 224 | 1123.8
[7 empty] | 225 | 1132 | 225 | 1132
[7 empty] | 226 | 1140.2 | 226 | 1140.2
[7 empty] | 227 | 1148.4 | 227 | 1148.4
[7 empty] | 228 | 1156.6 | 228 | 1156.6
[7 empty] | 229 | 1164.8 | 229 | 1164.8
[7 empty] | 230 | 1173 | 230 | 1173
[7 empty] | 231 | 1181.1 | 231 | 1181.1
[7 empty] | 232 | 1189.2 | 232 | 1189.2
[7 empty] | 233 | 1197.3 | 233 | 1197.3
[7 empty] | 234 | 1205.4 | 234 | 1205.4
[7 empty] | 235 | 1213.5 | 235 | 1213.5
[7 empty] | 236 | 1221.6 | 236 | 1221.6
[7 empty] | 237 | 1229.7 | 237 | 1229.7
[7 empty] | 238 | 1237.8 | 238 | 1237.8
[7 empty] | 239 | 1245.9 | 239 | 1245.9
[7 empty] | 240 | 1254 | 240 | 1254
[7 empty] | 241 | 1262.1 | 241 | 1262.1
[7 empty] | 242 | 1270.2 | 242 | 1270.2
[7 empty] | 243 | 1278.3 | 243 | 1278.3
[7 empty] | 244 | 1286.4 | 244 | 1286.4
[7 empty] | 245 | 1294.5 | 245 | 1294.5
[7 empty] | 246 | 1302.6 | 246 | 1302.6
[7 empty] | 247 | 1310.7 | 247 | 1310.7
[7 empty] | 248 | 1318.8 | 248 | 1318.8
[7 empty] | 249 | 1326.9 | 249 | 1326.9
[7 empty] | 250 | 1335 | 250 | 1335
[7 empty] | 251 | 1343.3 | 251 | 1343.3
[7 empty] | 252 | 1351.6 | 252 | 1351.6
[7 empty] | 253 | 1359.9 | 253 | 1359.9
[7 empty] | 254 | 1368.2 | 254 | 1368.2
[7 empty] | 255 | 1376.5 | 255 | 1376.5
[7 empty] | 256 | 1384.8 | 256 | 1384.8
[7 empty] | 257 | 1393.1 | 257 | 1393.1
[7 empty] | 258 | 1401.4 | 258 | 1401.4
[7 empty] | 259 | 1409.7 | 259 | 1409.7
[7 empty] | 260 | 1418 | 260 | 1418
[7 empty] | 261 | 1426.2 | 261 | 1426.2
[7 empty] | 262 | 1434.4 | 262 | 1434.4
[7 empty] | 263 | 1442.6 | 263 | 1442.6
[7 empty] | 264 | 1450.8 | 264 | 1450.8
[7 empty] | 265 | 1459 | 265 | 1459
[7 empty] | 266 | 1467.2 | 266 | 1467.2
[7 empty] | 267 | 1475.4 | 267 | 1475.4
[7 empty] | 268 | 1483.6 | 268 | 1483.6
[7 empty] | 269 | 1491.8 | 269 | 1491.8
[7 empty] | 270 | 1500 | 270 | 1500
[7 empty] | 271 | 1508.3 | 271 | 1508.3
[7 empty] | 272 | 1516.6 | 272 | 1516.6
[7 empty] | 273 | 1524.9 | 273 | 1524.9
[7 empty] | 274 | 1533.2 | 274 | 1533.2
[7 empty] | 275 | 1541.5 | 275 | 1541.5
[7 empty] | 276 | 1549.8 | 276 | 1549.8
[7 empty] | 277 | 1558.1 | 277 | 1558.1
[7 empty] | 278 | 1566.4 | 278 | 1566.4
[7 empty] | 279 | 1574.7 | 279 | 1574.7
[7 empty] | 280 | 1583 | 280 | 1583
[7 empty] | 281 | 1591.5 | 281 | 1591.5
[7 empty] | 282 | 1600 | 282 | 1600
[7 empty] | 283 | 1608.5 | 283 | 1608.5
[7 empty] | 284 | 1617 | 284 | 1617
[7 empty] | 285 | 1625.5 | 285 | 1625.5
[7 empty] | 286 | 1634 | 286 | 1634
[7 empty] | 287 | 1642.5 | 287 | 1642.5
[7 empty] | 288 | 1651 | 288 | 1651
[7 empty] | 289 | 1659.5 | 289 | 1659.5
[7 empty] | 290 | 1668 | 290 | 1668
[7 empty] | 291 | 1676.7 | 291 | 1676.7
[7 empty] | 292 | 1685.4 | 292 | 1685.4
[7 empty] | 293 | 1694.1 | 293 | 1694.1
[7 empty] | 294 | 1702.8 | 294 | 1702.8
[7 empty] | 295 | 1711.5 | 295 | 1711.5
[7 empty] | 296 | 1720.2 | 296 | 1720.2
[7 empty] | 297 | 1728.9 | 297 | 1728.9
[7 empty] | 298 | 1737.6 | 298 | 1737.6
[7 empty] | 299 | 1746.3 | 299 | 1746.3
[7 empty] | 300 | 1755 | 300 | 1755
[7 empty] | 301 | 1764 | 301 | 1764
[7 empty] | 302 | 1773 | 302 | 1773
[7 empty] | 303 | 1782 | 303 | 1782
[7 empty] | 304 | 1791 | 304 | 1791
[7 empty] | 305 | 1800 | 305 | 1800
[7 empty] | 306 | 1809 | 306 | 1809
[7 empty] | 307 | 1818 | 307 | 1818
[7 empty] | 308 | 1827 | 308 | 1827
[7 empty] | 309 | 1836 | 309 | 1836
[7 empty] | 310 | 1845 | 310 | 1845
[7 empty] | 311 | 1853.1 | 311 | 1853.1
[7 empty] | 312 | 1861.2 | 312 | 1861.2
[7 empty] | 313 | 1869.3 | 313 | 1869.3
[7 empty] | 314 | 1877.4 | 314 | 1877.4
[7 empty] | 315 | 1885.5 | 315 | 1885.5
[7 empty] | 316 | 1893.6 | 316 | 1893.6
[7 empty] | 317 | 1901.7 | 317 | 1901.7
[7 empty] | 318 | 1909.8 | 318 | 1909.8
[7 empty] | 319 | 1917.9 | 319 | 1917.9
[7 empty] | 320 | 1926 | 320 | 1926
[7 empty] | 321 | 1935.2 | 321 | 1935.2
[7 empty] | 322 | 1944.4 | 322 | 1944.4
[7 empty] | 323 | 1953.6 | 323 | 1953.6
[7 empty] | 324 | 1962.8 | 324 | 1962.8
[7 empty] | 325 | 1972 | 325 | 1972
[7 empty] | 326 | 1981.2 | 326 | 1981.2
[7 empty] | 327 | 1990.4 | 327 | 1990.4
[7 empty] | 328 | 1999.6 | 328 | 1999.6
[7 empty] | 329 | 2008.8 | 329 | 2008.8
[7 empty] | 330 | 2018 | 330 | 2018
[7 empty] | 331 | 2027.2 | 331 | 2027.2
[7 empty] | 332 | 2036.4 | 332 | 2036.4
[7 empty] | 333 | 2045.6 | 333 | 2045.6
[7 empty] | 334 | 2054.8 | 334 | 2054.8
[7 empty] | 335 | 2064 | 335 | 2064
[7 empty] | 336 | 2073.2 | 336 | 2073.2
[7 empty] | 337 | 2082.4 | 337 | 2082.4
[7 empty] | 338 | 2091.6 | 338 | 2091.6
[7 empty] | 339 | 2100.8 | 339 | 2100.8
[7 empty] | 340 | 2110 | 340 | 2110
[7 empty] | 341 | 2119.4 | 341 | 2119.4
[7 empty] | 342 | 2128.8 | 342 | 2128.8
[7 empty] | 343 | 2138.2 | 343 | 2138.2
[7 empty] | 344 | 2147.6 | 344 | 2147.6
[7 empty] | 345 | 2157 | 345 | 2157
[7 empty] | 346 | 2166.4 | 346 | 2166.4
[7 empty] | 347 | 2175.8 | 347 | 2175.8
[7 empty] | 348 | 2185.2 | 348 | 2185.2
[7 empty] | 349 | 2194.6 | 349 | 2194.6
[7 empty] | 350 | 2204 | 350 | 2204
[7 empty] | 351 | 2213.4 | 351 | 2213.4
[7 empty] | 352 | 2222.8 | 352 | 2222.8
[7 empty] | 353 | 2232.2 | 353 | 2232.2
[7 empty] | 354 | 2241.6 | 354 | 2241.6
[7 empty] | 355 | 2251 | 355 | 2251
[7 empty] | 356 | 2260.4 | 356 | 2260.4
[7 empty] | 357 | 2269.8 | 357 | 2269.8
[7 empty] | 358 | 2279.2 | 358 | 2279.2
[7 empty] | 359 | 2288.6 | 359 | 2288.6
[7 empty] | 360 | 2298 | 360 | 2298
[7 empty] | 361 | 2307 | 361 | 2307
[7 empty] | 362 | 2316 | 362 | 2316
[7 empty] | 363 | 2325 | 363 | 2325
[7 empty] | 364 | 2334 | 364 | 2334
[7 empty] | 365 | 2343 | 365 | 2343
[7 empty] | 366 | 2352 | 366 | 2352
[7 empty] | 367 | 2361 | 367 | 2361
[7 empty] | 368 | 2370 | 368 | 2370
[7 empty] | 369 | 2379 | 369 | 2379
[7 empty] | 370 | 2388 | 370 | 2388
[7 empty] | 371 | 2397.2 | 371 | 2397.2
[7 empty] | 372 | 2406.4 | 372 | 2406.4
[7 empty] | 373 | 2415.6 | 373 | 2415.6
[7 empty] | 374 | 2424.8 | 374 | 2424.8
[7 empty] | 375 | 2434 | 375 | 2434
[7 empty] | 376 | 2443.2 | 376 | 2443.2
[7 empty] | 377 | 2452.4 | 377 | 2452.4
[7 empty] | 378 | 2461.6 | 378 | 2461.6
[7 empty] | 379 | 2470.8 | 379 | 2470.8
[7 empty] | 380 | 2480 | 380 | 2480
[7 empty] | 381 | 2489.5 | 381 | 2492.2
[7 empty] | 382 | 2499 | 382 | 2501.4
[7 empty] | 383 | 2508.5 | 383 | 2510.6
[7 empty] | 384 | 2518 | 384 | 2519.8
[7 empty] | 385 | 2527.5 | 385 | 2529
[7 empty] | 386 | 2537 | 386 | 2538.2
[7 empty] | 387 | 2546.5 | 387 | 2547.4
[7 empty] | 388 | 2556 | 388 | 2556.6
[7 empty] | 389 | 2565.5 | 389 | 2565.8
[7 empty] | 390 | 2575 | 390 | 2575
[7 empty] | 391 | 2584.5 | 391 | 2584.5
[7 empty] | 392 | 2594 | 392 | 2594
[7 empty] | 393 | 2603.5 | 393 | 2603.5
[7 empty] | 394 | 2613 | 394 | 2613
[7 empty] | 395 | 2622.5 | 395 | 2622.5
[7 empty] | 396 | 2632 | 396 | 2632
[7 empty] | 397 | 2641.5 | 397 | 2641.5
[7 empty] | 398 | 2651 | 398 | 2651
[7 empty] | 399 | 2660.5 | 399 | 2660.5
[7 empty] | 400 | 2670 | 400 | 2670
[7 empty] | 401 | 2679.5 | 401 | 2690.2886
[7 empty] | 402 | 2689 | 402 | 2698.5899
[7 empty] | 403 | 2698.5 | 403 | 2706.8911
[7 empty] | 404 | 2708 | 404 | 2715.1924
[7 empty] | 405 | 2717.5 | 405 | 2723.4937
[7 empty] | 406 | 2727 | 406 | 2731.7949
[7 empty] | 407 | 2736.5 | 407 | 2740.0962
[7 empty] | 408 | 2746 | 408 | 2748.3975
[7 empty] | 409 | 2755.5 | 409 | 2756.6987
[7 empty] | 410 | 2765 | 410 | 2765
[7 empty] | 411 | 2774.7 | 411 | 2787.2886
[7 empty] | 412 | 2784.4 | 412 | 2795.5899
[7 empty] | 413 | 2794.1 | 413 | 2803.8911
[7 empty] | 414 | 2803.8 | 414 | 2812.1924
[7 empty] | 415 | 2813.5 | 415 | 2820.4937
[7 empty] | 416 | 2823.2 | 416 | 2828.7949
[7 empty] | 417 | 2832.9 | 417 | 2837.0962
[7 empty] | 418 | 2842.6 | 418 | 2845.3975
[7 empty] | 419 | 2852.3 | 419 | 2853.6987
[7 empty] | 420 | 2862 | 420 | 2862
[7 empty] | 421 | 2871.8 | 421 | 2871.8
[7 empty] | 422 | 2881.6 | 422 | 2881.6
[7 empty] | 423 | 2891.4 | 423 | 2891.4
[7 empty] | 424 | 2901.2 | 424 | 2901.2
[7 empty] | 425 | 2911 | 425 | 2911
[7 empty] | 426 | 2920.8 | 426 | 2920.8
[7 empty] | 427 | 2930.6 | 427 | 2930.6
[7 empty] | 428 | 2940.4 | 428 | 2940.4
[7 empty] | 429 | 2950.2 | 429 | 2950.2
[7 empty] | 430 | 2960 | 430 | 2960
[7 empty] | 431 | 2970 | 431 | 2970
[7 empty] | 432 | 2980 | 432 | 2980
[7 empty] | 433 | 2990 | 433 | 2990
[7 empty] | 434 | 3000 | 434 | 3000
[7 empty] | 435 | 3010 | 435 | 3010
[7 empty] | 436 | 3020 | 436 | 3020
[7 empty] | 437 | 3030 | 437 | 3030
[7 empty] | 438 | 3040 | 438 | 3040
[7 empty] | 439 | 3050 | 439 | 3050
[7 empty] | 440 | 3060 | 440 | 3060
[7 empty] | 441 | 3069 | 441 | 3069
[7 empty] | 442 | 3078 | 442 | 3078
[7 empty] | 443 | 3087 | 443 | 3087
[7 empty] | 444 | 3096 | 444 | 3096
[7 empty] | 445 | 3105 | 445 | 3105
[7 empty] | 446 | 3114 | 446 | 3114
[7 empty] | 447 | 3123 | 447 | 3123
[7 empty] | 448 | 3132 | 448 | 3132
[7 empty] | 449 | 3141 | 449 | 3141
[7 empty] | 450 | 3150 | 450 | 3150
[7 empty] | 451 | 3159.4 | 451 | 3159.4
[7 empty] | 452 | 3168.8 | 452 | 3168.8
[7 empty] | 453 | 3178.2 | 453 | 3178.2
[7 empty] | 454 | 3187.6 | 454 | 3187.6
[7 empty] | 455 | 3197 | 455 | 3197
[7 empty] | 456 | 3206.4 | 456 | 3206.4
[7 empty] | 457 | 3215.8 | 457 | 3215.8
[7 empty] | 458 | 3225.2 | 458 | 3225.2
[7 empty] | 459 | 3234.6 | 459 | 3234.6
[7 empty] | 460 | 3244 | 460 | 3244
[7 empty] | 461 | 3253.4 | 461 | 3253.4
[7 empty] | 462 | 3262.8 | 462 | 3262.8
[7 empty] | 463 | 3272.2 | 463 | 3272.2
[7 empty] | 464 | 3281.6 | 464 | 3281.6
[7 empty] | 465 | 3291 | 465 | 3291
[7 empty] | 466 | 3300.4 | 466 | 3300.4
[7 empty] | 467 | 3309.8 | 467 | 3309.8
[7 empty] | 468 | 3319.2 | 468 | 3319.2
[7 empty] | 469 | 3328.6 | 469 | 3328.6
[7 empty] | 470 | 3338 | 470 | 3338
[7 empty] | 471 | 3347.4 | 471 | 3347.4
[7 empty] | 472 | 3356.8 | 472 | 3356.8
[7 empty] | 473 | 3366.2 | 473 | 3366.2
[7 empty] | 474 | 3375.6 | 474 | 3375.6
[7 empty] | 475 | 3385 | 475 | 3385
[7 empty] | 476 | 3394.4 | 476 | 3394.4
[7 empty] | 477 | 3403.8 | 477 | 3403.8
[7 empty] | 478 | 3413.2 | 478 | 3413.2
[7 empty] | 479 | 3422.6 | 479 | 3422.6
[7 empty] | 480 | 3432 | 480 | 3432
[7 empty] | 481 | 3441.4 | 481 | 3441.4
[7 empty] | 482 | 3450.8 | 482 | 3450.8
[7 empty] | 483 | 3460.2 | 483 | 3460.2
[7 empty] | 484 | 3469.6 | 484 | 3469.6
[7 empty] | 485 | 3479 | 485 | 3479
[7 empty] | 486 | 3488.4 | 486 | 3488.4
[7 empty] | 487 | 3497.8 | 487 | 3497.8
[7 empty] | 488 | 3507.2 | 488 | 3507.2
[7 empty] | 489 | 3516.6 | 489 | 3516.6
[7 empty] | 490 | 3526 | 490 | 3526
[7 empty] | 491 | 3535.4 | 491 | 3535.4
[7 empty] | 492 | 3544.8 | 492 | 3544.8
[7 empty] | 493 | 3554.2 | 493 | 3554.2
[7 empty] | 494 | 3563.6 | 494 | 3563.6
[7 empty] | 495 | 3573 | 495 | 3573
[7 empty] | 496 | 3582.4 | 496 | 3582.4
[7 empty] | 497 | 3591.8 | 497 | 3591.8
[7 empty] | 498 | 3601.2 | 498 | 3601.2
[7 empty] | 499 | 3610.6 | 499 | 3610.6
[7 empty] | 500 | 3620 | 500 | 3620
[7 empty] | 501 | 3629 | 501 | 3629
[7 empty] | 502 | 3638 | 502 | 3638
[7 empty] | 503 | 3647 | 503 | 3647
[7 empty] | 504 | 3656 | 504 | 3656
[7 empty] | 505 | 3665 | 505 | 3665
[7 empty] | 506 | 3674 | 506 | 3674
[7 empty] | 507 | 3683 | 507 | 3683
[7 empty] | 508 | 3692 | 508 | 3692
[7 empty] | 509 | 3701 | 509 | 3701
[7 empty] | 510 | 3710 | 510 | 3710
[7 empty] | 511 | 3719 | 511 | 3719
[7 empty] | 512 | 3728 | 512 | 3728
[7 empty] | 513 | 3737 | 513 | 3737
[7 empty] | 514 | 3746 | 514 | 3746
[7 empty] | 515 | 3755 | 515 | 3755
[7 empty] | 516 | 3764 | 516 | 3764
[7 empty] | 517 | 3773 | 517 | 3773
[7 empty] | 518 | 3782 | 518 | 3782
[7 empty] | 519 | 3791 | 519 | 3791
[7 empty] | 520 | 3800 | 520 | 3800
[7 empty] | 521 | 3809 | 521 | 3809
[7 empty] | 522 | 3818 | 522 | 3818
[7 empty] | 523 | 3827 | 523 | 3827
[7 empty] | 524 | 3836 | 524 | 3836
[7 empty] | 525 | 3845 | 525 | 3845
[7 empty] | 526 | 3854 | 526 | 3854
[7 empty] | 527 | 3863 | 527 | 3863
[7 empty] | 528 | 3872 | 528 | 3872
[7 empty] | 529 | 3881 | 529 | 3881
[7 empty] | 530 | 3890 | 530 | 3890
[7 empty] | 531 | 3899 | 531 | 3899
[7 empty] | 532 | 3908 | 532 | 3908
[7 empty] | 533 | 3917 | 533 | 3917
[7 empty] | 534 | 3926 | 534 | 3926
[7 empty] | 535 | 3935 | 535 | 3935
[7 empty] | 536 | 3944 | 536 | 3944
[7 empty] | 537 | 3953 | 537 | 3953
[7 empty] | 538 | 3962 | 538 | 3962
[7 empty] | 539 | 3971 | 539 | 3971
[7 empty] | 540 | 3980 | 540 | 3980
[7 empty] | 541 | 3989 | 541 | 3989
[7 empty] | 542 | 3998 | 542 | 3998
[7 empty] | 543 | 4007 | 543 | 4007
[7 empty] | 544 | 4016 | 544 | 4016
[7 empty] | 545 | 4025 | 545 | 4025
[7 empty] | 546 | 4034 | 546 | 4034
[7 empty] | 547 | 4043 | 547 | 4043
[7 empty] | 548 | 4052 | 548 | 4052
[7 empty] | 549 | 4061 | 549 | 4061
[7 empty] | 550 | 4070 | 550 | 4070
[7 empty] | 551 | 4078.2 | 551 | 4078.2
[7 empty] | 552 | 4086.4 | 552 | 4086.4
[7 empty] | 553 | 4094.6 | 553 | 4094.6
[7 empty] | 554 | 4102.8 | 554 | 4102.8
[7 empty] | 555 | 4111 | 555 | 4111
[7 empty] | 556 | 4119.2 | 556 | 4119.2
[7 empty] | 557 | 4127.4 | 557 | 4127.4
[7 empty] | 558 | 4135.6 | 558 | 4135.6
[7 empty] | 559 | 4143.8 | 559 | 4143.8
[7 empty] | 560 | 4152 | 560 | 4152
[7 empty] | 561 | 4160.2 | 561 | 4160.2
[7 empty] | 562 | 4168.4 | 562 | 4168.4
[7 empty] | 563 | 4176.6 | 563 | 4176.6
[7 empty] | 564 | 4184.8 | 564 | 4184.8
[7 empty] | 565 | 4193 | 565 | 4193
[7 empty] | 566 | 4201.2 | 566 | 4201.2
[7 empty] | 567 | 4209.4 | 567 | 4209.4
[7 empty] | 568 | 4217.6 | 568 | 4217.6
[7 empty] | 569 | 4225.8 | 569 | 4225.8
[7 empty] | 570 | 4234 | 570 | 4234
[7 empty] | 571 | 4242.2 | 571 | 4242.2
[7 empty] | 572 | 4250.4 | 572 | 4250.4
[7 empty] | 573 | 4258.6 | 573 | 4258.6
[7 empty] | 574 | 4266.8 | 574 | 4266.8
[7 empty] | 575 | 4275 | 575 | 4275
[7 empty] | 576 | 4283.2 | 576 | 4283.2
[7 empty] | 577 | 4291.4 | 577 | 4291.4
[7 empty] | 578 | 4299.6 | 578 | 4299.6
[7 empty] | 579 | 4307.8 | 579 | 4307.8
[7 empty] | 580 | 4316 | 580 | 4316
[7 empty] | 581 | 4324.2 | 581 | 4324.2
[7 empty] | 582 | 4332.4 | 582 | 4332.4
[7 empty] | 583 | 4340.6 | 583 | 4340.6
[7 empty] | 584 | 4348.8 | 584 | 4348.8
[7 empty] | 585 | 4357 | 585 | 4357
[7 empty] | 586 | 4365.2 | 586 | 4365.2
[7 empty] | 587 | 4373.4 | 587 | 4373.4
[7 empty] | 588 | 4381.6 | 588 | 4381.6
[7 empty] | 589 | 4389.8 | 589 | 4389.8
[7 empty] | 590 | 4398 | 590 | 4398
[7 empty] | 591 | 4406.2 | 591 | 4406.2
[7 empty] | 592 | 4414.4 | 592 | 4414.4
[7 empty] | 593 | 4422.6 | 593 | 4422.6
[7 empty] | 594 | 4430.8 | 594 | 4430.8
[7 empty] | 595 | 4439 | 595 | 4439
[7 empty] | 596 | 4447.2 | 596 | 4447.2
[7 empty] | 597 | 4455.4 | 597 | 4455.4
[7 empty] | 598 | 4463.6 | 598 | 4463.6
[7 empty] | 599 | 4471.8 | 599 | 4471.8
[7 empty] | 600 | 4480 | 600 | 4480
[7 empty] | 601 | 4489 | 601 | 4489
[7 empty] | 602 | 4498 | 602 | 4498
[7 empty] | 603 | 4507 | 603 | 4507
[7 empty] | 604 | 4516 | 604 | 4516
[7 empty] | 605 | 4525 | 605 | 4525
[7 empty] | 606 | 4534 | 606 | 4534
[7 empty] | 607 | 4543 | 607 | 4543
[7 empty] | 608 | 4552 | 608 | 4552
[7 empty] | 609 | 4561 | 609 | 4561
[7 empty] | 610 | 4570 | 610 | 4570
[7 empty] | 611 | 4579 | 611 | 4579
[7 empty] | 612 | 4588 | 612 | 4588
[7 empty] | 613 | 4597 | 613 | 4597
[7 empty] | 614 | 4606 | 614 | 4606
[7 empty] | 615 | 4615 | 615 | 4615
[7 empty] | 616 | 4624 | 616 | 4624
[7 empty] | 617 | 4633 | 617 | 4633
[7 empty] | 618 | 4642 | 618 | 4642
[7 empty] | 619 | 4651 | 619 | 4651
[7 empty] | 620 | 4660 | 620 | 4660
[7 empty] | 621 | 4669 | 621 | 4669
[7 empty] | 622 | 4678 | 622 | 4678
[7 empty] | 623 | 4687 | 623 | 4687
[7 empty] | 624 | 4696 | 624 | 4696
[7 empty] | 625 | 4705 | 625 | 4705
[7 empty] | 626 | 4714 | 626 | 4714
[7 empty] | 627 | 4723 | 627 | 4723
[7 empty] | 628 | 4732 | 628 | 4732
[7 empty] | 629 | 4741 | 629 | 4741
[7 empty] | 630 | 4750 | 630 | 4750
[7 empty] | 631 | 4759 | 631 | 4759
[7 empty] | 632 | 4768 | 632 | 4768
[7 empty] | 633 | 4777 | 633 | 4777
[7 empty] | 634 | 4786 | 634 | 4786
[7 empty] | 635 | 4795 | 635 | 4795
[7 empty] | 636 | 4804 | 636 | 4804
[7 empty] | 637 | 4813 | 637 | 4813
[7 empty] | 638 | 4822 | 638 | 4822
[7 empty] | 639 | 4831 | 639 | 4831
[7 empty] | 640 | 4840 | 640 | 4840
[7 empty] | 641 | 4849 | 641 | 4849
[7 empty] | 642 | 4858 | 642 | 4858
[7 empty] | 643 | 4867 | 643 | 4867
[7 empty] | 644 | 4876 | 644 | 4876
[7 empty] | 645 | 4885 | 645 | 4885
[7 empty] | 646 | 4894 | 646 | 4894
[7 empty] | 647 | 4903 | 647 | 4903
[7 empty] | 648 | 4912 | 648 | 4912
[7 empty] | 649 | 4921 | 649 | 4921
[7 empty] | 650 | 4930 | 650 | 4930
[7 empty] | 651 | 4939 | 651 | 4939
[7 empty] | 652 | 4948 | 652 | 4948
[7 empty] | 653 | 4957 | 653 | 4957
[7 empty] | 654 | 4966 | 654 | 4966
[7 empty] | 655 | 4975 | 655 | 4975
[7 empty] | 656 | 4984 | 656 | 4984
[7 empty] | 657 | 4993 | 657 | 4993
[7 empty] | 658 | 5002 | 658 | 5002
[7 empty] | 659 | 5011 | 659 | 5011
[7 empty] | 660 | 5020 | 660 | 5020
[7 empty] | 661 | 5029 | 661 | 5029
[7 empty] | 662 | 5038 | 662 | 5038
[7 empty] | 663 | 5047 | 663 | 5047
[7 empty] | 664 | 5056 | 664 | 5056
[7 empty] | 665 | 5065 | 665 | 5065
[7 empty] | 666 | 5074 | 666 | 5074
[7 empty] | 667 | 5083 | 667 | 5083
[7 empty] | 668 | 5092 | 668 | 5092
[7 empty] | 669 | 5101 | 669 | 5101
[7 empty] | 670 | 5110 | 670 | 5110
[7 empty] | 671 | 5119 | 671 | 5119
[7 empty] | 672 | 5128 | 672 | 5128
[7 empty] | 673 | 5137 | 673 | 5137
[7 empty] | 674 | 5146 | 674 | 5146
[7 empty] | 675 | 5155 | 675 | 5155
[7 empty] | 676 | 5164 | 676 | 5164
[7 empty] | 677 | 5173 | 677 | 5173
[7 empty] | 678 | 5182 | 678 | 5182
[7 empty] | 679 | 5191 | 679 | 5191
[7 empty] | 680 | 5200 | 680 | 5200
[7 empty] | 681 | 5209 | 681 | 5209
[7 empty] | 682 | 5218 | 682 | 5218
[7 empty] | 683 | 5227 | 683 | 5227
[7 empty] | 684 | 5236 | 684 | 5236
[7 empty] | 685 | 5245 | 685 | 5245
[7 empty] | 686 | 5254 | 686 | 5254
[7 empty] | 687 | 5263 | 687 | 5263
[7 empty] | 688 | 5272 | 688 | 5272
[7 empty] | 689 | 5281 | 689 | 5281
[7 empty] | 690 | 5290 | 690 | 5290
[7 empty] | 691 | 5299 | 691 | 5299
[7 empty] | 692 | 5308 | 692 | 5308
[7 empty] | 693 | 5317 | 693 | 5317
[7 empty] | 694 | 5326 | 694 | 5326
[7 empty] | 695 | 5335 | 695 | 5335
[7 empty] | 696 | 5344 | 696 | 5344
[7 empty] | 697 | 5353 | 697 | 5353
[7 empty] | 698 | 5362 | 698 | 5362
[7 empty] | 699 | 5371 | 699 | 5371
[7 empty] | 700 | 5380 | 700 | 5380
[7 empty] | 701 | 5389 | 701 | 5389
[7 empty] | 702 | 5398 | 702 | 5398
[7 empty] | 703 | 5407 | 703 | 5407
[7 empty] | 704 | 5416 | 704 | 5416
[7 empty] | 705 | 5425 | 705 | 5425
[7 empty] | 706 | 5434 | 706 | 5434
[7 empty] | 707 | 5443 | 707 | 5443
[7 empty] | 708 | 5452 | 708 | 5452
[7 empty] | 709 | 5461 | 709 | 5461
[7 empty] | 710 | 5470 | 710 | 5470
[7 empty] | 711 | 5479 | 711 | 5479
[7 empty] | 712 | 5488 | 712 | 5488
[7 empty] | 713 | 5497 | 713 | 5497
[7 empty] | 714 | 5506 | 714 | 5506
[7 empty] | 715 | 5515 | 715 | 5515
[7 empty] | 716 | 5524 | 716 | 5524
[7 empty] | 717 | 5533 | 717 | 5533
[7 empty] | 718 | 5542 | 718 | 5542
[7 empty] | 719 | 5551 | 719 | 5551
[7 empty] | 720 | 5560 | 720 | 5560
[7 empty] | 721 | 5569 | 721 | 5569
[7 empty] | 722 | 5578 | 722 | 5578
[7 empty] | 723 | 5587 | 723 | 5587
[7 empty] | 724 | 5596 | 724 | 5596
[7 empty] | 725 | 5605 | 725 | 5605
[7 empty] | 726 | 5614 | 726 | 5614
[7 empty] | 727 | 5623 | 727 | 5623
[7 empty] | 728 | 5632 | 728 | 5632
[7 empty] | 729 | 5641 | 729 | 5641
[7 empty] | 730 | 5650 | 730 | 5650
[7 empty] | 731 | 5659 | 731 | 5659
[7 empty] | 732 | 5668 | 732 | 5668
[7 empty] | 733 | 5677 | 733 | 5677
[7 empty] | 734 | 5686 | 734 | 5686
[7 empty] | 735 | 5695 | 735 | 5695
[7 empty] | 736 | 5704 | 736 | 5704
[7 empty] | 737 | 5713 | 737 | 5713
[7 empty] | 738 | 5722 | 738 | 5722
[7 empty] | 739 | 5731 | 739 | 5731
[7 empty] | 740 | 5740 | 740 | 5740
[7 empty] | 741 | 5749 | 741 | 5749
[7 empty] | 742 | 5758 | 742 | 5758
[7 empty] | 743 | 5767 | 743 | 5767
[7 empty] | 744 | 5776 | 744 | 5776
[7 empty] | 745 | 5785 | 745 | 5785
[7 empty] | 746 | 5794 | 746 | 5794
[7 empty] | 747 | 5803 | 747 | 5803
[7 empty] | 748 | 5812 | 748 | 5812
[7 empty] | 749 | 5821 | 749 | 5821
[7 empty] | 750 | 5830 | 750 | 5830
[7 empty] | 751 | 5839 | 751 | 5839
[7 empty] | 752 | 5848 | 752 | 5848
[7 empty] | 753 | 5857 | 753 | 5857
[7 empty] | 754 | 5866 | 754 | 5866
[7 empty] | 755 | 5875 | 755 | 5875
[7 empty] | 756 | 5884 | 756 | 5884
[7 empty] | 757 | 5893 | 757 | 5893
[7 empty] | 758 | 5902 | 758 | 5902
[7 empty] | 759 | 5911 | 759 | 5911
[7 empty] | 760 | 5920 | 760 | 5920
[7 empty] | 761 | 5929 | 761 | 5929
[7 empty] | 762 | 5938 | 762 | 5938
[7 empty] | 763 | 5947 | 763 | 5947
[7 empty] | 764 | 5956 | 764 | 5956
[7 empty] | 765 | 5965 | 765 | 5965
[7 empty] | 766 | 5974 | 766 | 5974
[7 empty] | 767 | 5983 | 767 | 5983
[7 empty] | 768 | 5992 | 768 | 5992
[7 empty] | 769 | 6001 | 769 | 6001
[7 empty] | 770 | 6010 | 770 | 6010
[7 empty] | 771 | 6019 | 771 | 6019
[7 empty] | 772 | 6028 | 772 | 6028
[7 empty] | 773 | 6037 | 773 | 6037
[7 empty] | 774 | 6046 | 774 | 6046
[7 empty] | 775 | 6055 | 775 | 6055
[7 empty] | 776 | 6064 | 776 | 6064
[7 empty] | 777 | 6073 | 777 | 6073
[7 empty] | 778 | 6082 | 778 | 6082
[7 empty] | 779 | 6091 | 779 | 6091
[7 empty] | 780 | 6100 | 780 | 6100
[7 empty] | 781 | 6109 | 781 | 6109
[7 empty] | 782 | 6118 | 782 | 6118
[7 empty] | 783 | 6127 | 783 | 6127
[7 empty] | 784 | 6136 | 784 | 6136
[7 empty] | 785 | 6145 | 785 | 6145
[7 empty] | 786 | 6154 | 786 | 6154
[7 empty] | 787 | 6163 | 787 | 6163
[7 empty] | 788 | 6172 | 788 | 6172
[7 empty] | 789 | 6181 | 789 | 6181
[7 empty] | 790 | 6190 | 790 | 6190
[7 empty] | 791 | 6199 | 791 | 6199
[7 empty] | 792 | 6208 | 792 | 6208
[7 empty] | 793 | 6217 | 793 | 6217
[7 empty] | 794 | 6226 | 794 | 6226
[7 empty] | 795 | 6235 | 795 | 6235
[7 empty] | 796 | 6244 | 796 | 6244
[7 empty] | 797 | 6253 | 797 | 6253
[7 empty] | 798 | 6262 | 798 | 6262
[7 empty] | 799 | 6271 | 799 | 6271
[7 empty] | 800 | 6280 | 800 | 6280
[7 empty] | 801 | 6290 | 801 | 6290
[7 empty] | 802 | 6300 | 802 | 6300
[7 empty] | 803 | 6310 | 803 | 6310
[7 empty] | 804 | 6320 | 804 | 6320
[7 empty] | 805 | 6330 | 805 | 6330
[7 empty] | 806 | 6340 | 806 | 6340
[7 empty] | 807 | 6350 | 807 | 6350
[7 empty] | 808 | 6360 | 808 | 6360
[7 empty] | 809 | 6370 | 809 | 6370
[7 empty] | 810 | 6380 | 810 | 6380
[7 empty] | 811 | 6390 | 811 | 6390
[7 empty] | 812 | 6400 | 812 | 6400
[7 empty] | 813 | 6410 | 813 | 6410
[7 empty] | 814 | 6420 | 814 | 6420
[7 empty] | 815 | 6430 | 815 | 6430
[7 empty] | 816 | 6440 | 816 | 6440
[7 empty] | 817 | 6450 | 817 | 6450
[7 empty] | 818 | 6460 | 818 | 6460
[7 empty] | 819 | 6470 | 819 | 6470
[7 empty] | 820 | 6480 | 820 | 6480
[7 empty] | 821 | 6490 | 821 | 6490
[7 empty] | 822 | 6500 | 822 | 6500
[7 empty] | 823 | 6510 | 823 | 6510
[7 empty] | 824 | 6520 | 824 | 6520
[7 empty] | 825 | 6530 | 825 | 6530
[7 empty] | 826 | 6540 | 826 | 6540
[7 empty] | 827 | 6550 | 827 | 6550
[7 empty] | 828 | 6560 | 828 | 6560
[7 empty] | 829 | 6570 | 829 | 6570
[7 empty] | 830 | 6580 | 830 | 6580
[7 empty] | 831 | 6590 | 831 | 6590
[7 empty] | 832 | 6600 | 832 | 6600
[7 empty] | 833 | 6610 | 833 | 6610
[7 empty] | 834 | 6620 | 834 | 6620
[7 empty] | 835 | 6630 | 835 | 6630
[7 empty] | 836 | 6640 | 836 | 6640
[7 empty] | 837 | 6650 | 837 | 6650
[7 empty] | 838 | 6660 | 838 | 6660
[7 empty] | 839 | 6670 | 839 | 6670
[7 empty] | 840 | 6680 | 840 | 6680
[7 empty] | 841 | 6690 | 841 | 6690
[7 empty] | 842 | 6700 | 842 | 6700
[7 empty] | 843 | 6710 | 843 | 6710
[7 empty] | 844 | 6720 | 844 | 6720
[7 empty] | 845 | 6730 | 845 | 6730
[7 empty] | 846 | 6740 | 846 | 6740
[7 empty] | 847 | 6750 | 847 | 6750
[7 empty] | 848 | 6760 | 848 | 6760
[7 empty] | 849 | 6770 | 849 | 6770
[7 empty] | 850 | 6780 | 850 | 6780
[7 empty] | 851 | 6790 | 851 | 6790
[7 empty] | 852 | 6800 | 852 | 6800
[7 empty] | 853 | 6810 | 853 | 6810
[7 empty] | 854 | 6820 | 854 | 6820
[7 empty] | 855 | 6830 | 855 | 6830
[7 empty] | 856 | 6840 | 856 | 6840
[7 empty] | 857 | 6850 | 857 | 6850
[7 empty] | 858 | 6860 | 858 | 6860
[7 empty] | 859 | 6870 | 859 | 6870
[7 empty] | 860 | 6880 | 860 | 6880
[7 empty] | 861 | 6890 | 861 | 6890
[7 empty] | 862 | 6900 | 862 | 6900
[7 empty] | 863 | 6910 | 863 | 6910
[7 empty] | 864 | 6920 | 864 | 6920
[7 empty] | 865 | 6930 | 865 | 6930
[7 empty] | 866 | 6940 | 866 | 6940
[7 empty] | 867 | 6950 | 867 | 6950
[7 empty] | 868 | 6960 | 868 | 6960
[7 empty] | 869 | 6970 | 869 | 6970
[7 empty] | 870 | 6980 | 870 | 6980
[7 empty] | 871 | 6990 | 871 | 6990
[7 empty] | 872 | 7000 | 872 | 7000
[7 empty] | 873 | 7010 | 873 | 7010
[7 empty] | 874 | 7020 | 874 | 7020
[7 empty] | 875 | 7030 | 875 | 7030
[7 empty] | 876 | 7040 | 876 | 7040
[7 empty] | 877 | 7050 | 877 | 7050
[7 empty] | 878 | 7060 | 878 | 7060
[7 empty] | 879 | 7070 | 879 | 7070
[7 empty] | 880 | 7080 | 880 | 7080
[7 empty] | 881 | 7090 | 881 | 7090
[7 empty] | 882 | 7100 | 882 | 7100
[7 empty] | 883 | 7110 | 883 | 7110
[7 empty] | 884 | 7120 | 884 | 7120
[7 empty] | 885 | 7130 | 885 | 7130
[7 empty] | 886 | 7140 | 886 | 7140
[7 empty] | 887 | 7150 | 887 | 7150
[7 empty] | 888 | 7160 | 888 | 7160
[7 empty] | 889 | 7170 | 889 | 7170
[7 empty] | 890 | 7180 | 890 | 7180
[7 empty] | 891 | 7190 | 891 | 7190
[7 empty] | 892 | 7200 | 892 | 7200
[7 empty] | 893 | 7210 | 893 | 7210
[7 empty] | 894 | 7220 | 894 | 7220
[7 empty] | 895 | 7230 | 895 | 7230
[7 empty] | 896 | 7240 | 896 | 7240
[7 empty] | 897 | 7250 | 897 | 7250
[7 empty] | 898 | 7260 | 898 | 7260
[7 empty] | 899 | 7270 | 899 | 7270
[7 empty] | 900 | 7280 | 900 | 7280
[7 empty] | 901 | 7290.2 | 901 | 7290.2
[7 empty] | 902 | 7300.4 | 902 | 7300.4
[7 empty] | 903 | 7310.6 | 903 | 7310.6
[7 empty] | 904 | 7320.8 | 904 | 7320.8
[7 empty] | 905 | 7331 | 905 | 7331
[7 empty] | 906 | 7341.2 | 906 | 7341.2
[7 empty] | 907 | 7351.4 | 907 | 7351.4
[7 empty] | 908 | 7361.6 | 908 | 7361.6
[7 empty] | 909 | 7371.8 | 909 | 7371.8
[7 empty] | 910 | 7382 | 910 | 7382
[7 empty] | 911 | 7392.2 | 911 | 7392.2
[7 empty] | 912 | 7402.4 | 912 | 7402.4
[7 empty] | 913 | 7412.6 | 913 | 7412.6
[7 empty] | 914 | 7422.8 | 914 | 7422.8
[7 empty] | 915 | 7433 | 915 | 7433
[7 empty] | 916 | 7443.2 | 916 | 7443.2
[7 empty] | 917 | 7453.4 | 917 | 7453.4
[7 empty] | 918 | 7463.6 | 918 | 7463.6
[7 empty] | 919 | 7473.8 | 919 | 7473.8
[7 empty] | 920 | 7484 | 920 | 7484
[7 empty] | 921 | 7494.2 | 921 | 7494.2
[7 empty] | 922 | 7504.4 | 922 | 7504.4
[7 empty] | 923 | 7514.6 | 923 | 7514.6
[7 empty] | 924 | 7524.8 | 924 | 7524.8
[7 empty] | 925 | 7535 | 925 | 7535
[7 empty] | 926 | 7545.2 | 926 | 7545.2
[7 empty] | 927 | 7555.4 | 927 | 7555.4
[7 empty] | 928 | 7565.6 | 928 | 7565.6
[7 empty] | 929 | 7575.8 | 929 | 7575.8
[7 empty] | 930 | 7586 | 930 | 7586
[7 empty] | 931 | 7596.2 | 931 | 7596.2
[7 empty] | 932 | 7606.4 | 932 | 7606.4
[7 empty] | 933 | 7616.6 | 933 | 7616.6
[7 empty] | 934 | 7626.8 | 934 | 7626.8
[7 empty] | 935 | 7637 | 935 | 7637
[7 empty] | 936 | 7647.2 | 936 | 7647.2
[7 empty] | 937 | 7657.4 | 937 | 7657.4
[7 empty] | 938 | 7667.6 | 938 | 7667.6
[7 empty] | 939 | 7677.8 | 939 | 7677.8
[7 empty] | 940 | 7688 | 940 | 7688
[7 empty] | 941 | 7698.2 | 941 | 7698.2
[7 empty] | 942 | 7708.4 | 942 | 7708.4
[7 empty] | 943 | 7718.6 | 943 | 7718.6
[7 empty] | 944 | 7728.8 | 944 | 7728.8
[7 empty] | 945 | 7739 | 945 | 7739
[7 empty] | 946 | 7749.2 | 946 | 7749.2
[7 empty] | 947 | 7759.4 | 947 | 7759.4
[7 empty] | 948 | 7769.6 | 948 | 7769.6
[7 empty] | 949 | 7779.8 | 949 | 7779.8
[7 empty] | 950 | 7790 | 950 | 7790
[7 empty] | 951 | 7800.2 | 951 | 7800.2
[7 empty] | 952 | 7810.4 | 952 | 7810.4
[7 empty] | 953 | 7820.6 | 953 | 7820.6
[7 empty] | 954 | 7830.8 | 954 | 7830.8
[7 empty] | 955 | 7841 | 955 | 7841
[7 empty] | 956 | 7851.2 | 956 | 7851.2
[7 empty] | 957 | 7861.4 | 957 | 7861.4
[7 empty] | 958 | 7871.6 | 958 | 7871.6
[7 empty] | 959 | 7881.8 | 959 | 7881.8
[7 empty] | 960 | 7892 | 960 | 7892
[7 empty] | 961 | 7902.2 | 961 | 7902.2
[7 empty] | 962 | 7912.4 | 962 | 7912.4
[7 empty] | 963 | 7922.6 | 963 | 7922.6
[7 empty] | 964 | 7932.8 | 964 | 7932.8
[7 empty] | 965 | 7943 | 965 | 7943
[7 empty] | 966 | 7953.2 | 966 | 7953.2
[7 empty] | 967 | 7963.4 | 967 | 7963.4
[7 empty] | 968 | 7973.6 | 968 | 7973.6
[7 empty] | 969 | 7983.8 | 969 | 7983.8
[7 empty] | 970 | 7994 | 970 | 7994
[7 empty] | 971 | 8004.2 | 971 | 8004.2
[7 empty] | 972 | 8014.4 | 972 | 8014.4
[7 empty] | 973 | 8024.6 | 973 | 8024.6
[7 empty] | 974 | 8034.8 | 974 | 8034.8
[7 empty] | 975 | 8045 | 975 | 8045
[7 empty] | 976 | 8055.2 | 976 | 8055.2
[7 empty] | 977 | 8065.4 | 977 | 8065.4
[7 empty] | 978 | 8075.6 | 978 | 8075.6
[7 empty] | 979 | 8085.8 | 979 | 8085.8
[7 empty] | 980 | 8096 | 980 | 8096
[7 empty] | 981 | 8106.2 | 981 | 8106.2
[7 empty] | 982 | 8116.4 | 982 | 8116.4
[7 empty] | 983 | 8126.6 | 983 | 8126.6
[7 empty] | 984 | 8136.8 | 984 | 8136.8
[7 empty] | 985 | 8147 | 985 | 8147
[7 empty] | 986 | 8157.2 | 986 | 8157.2
[7 empty] | 987 | 8167.4 | 987 | 8167.4
[7 empty] | 988 | 8177.6 | 988 | 8177.6
[7 empty] | 989 | 8187.8 | 989 | 8187.8
[7 empty] | 990 | 8198 | 990 | 8198
[7 empty] | 991 | 8208.2 | 991 | 8208.2
[7 empty] | 992 | 8218.4 | 992 | 8218.4
[7 empty] | 993 | 8228.6 | 993 | 8228.6
[7 empty] | 994 | 8238.8 | 994 | 8238.8
[7 empty] | 995 | 8249 | 995 | 8249
[7 empty] | 996 | 8259.2 | 996 | 8259.2
[7 empty] | 997 | 8269.4 | 997 | 8269.4
[7 empty] | 998 | 8279.6 | 998 | 8279.6
[7 empty] | 999 | 8289.8 | 999 | 8289.8
[7 empty] | 1000 | 8300 | 1000 | 8300